## 2021P Draft - ReadMe
This workbook is a technical document supporting the work of estimating the costs of energy efficiency measures for the draft 2021 Power Plan. Technical information displayed here relate to incremental cost and savings and total potential for a particular measure.
For more information, see the Council's Conservation Resources Advisory Committee (CRAC) webpage where presentations on measures are posted.
Questions? Contact Charlie Grist, cgrist@nwcouncil.org, 503.222.5161.

## SourceSummary
Measure: | Utility Distribution System
Item | Methods & Sources | Note | Updates since last Plan
Measures Described | Three measures to regulate voltage and upgrade systems to achieve energy and capacity savings. ECM1: LDC without Voltage/Var Optimization (VVO) Lowers the distribution voltage level only using LDC without any system improvements for voltage optimization. ECM2: LDC with Voltage Optimization Includes Option 1 and adds system improvements including var management and end of line metering. ECM3: LDC with Voltage Optimization and Existing EMI Includes Option 2 ands secondary voltage monitoring through existing AMI Becasue the levelized cost of ECM3 is lower than ECM2 the two measures are combined in the roll up in the Procost workbook for purpose of creating the supply curve used in RPM. | In common terms: ECM1: Do LDC for the specific purpose of lowering voltage for CVR, but do no other system upgrades. The rationale here is that LDC may or may not be being done across the region, and where it is being done, it may be for reliability and power quality, not conservation. Given that this is really primarily a substation setting (LTC and/or VR) with no closed loop feedback, the potential savings is relatively low. ECM2: Optimize voltage across the distribution system to be as flat as possible over distance so that the head voltage can be low without risking the end of line voltage falling out of ANSI. This can be realized with additional caps + SCADA for all regulating assets + an end of line voltage monitor and a coordinating control scheme. ECM3: With voltage optimization in place, leverage existing AMI to push even further since secondary voltage can be directly measured to ensure ANSI standards are continuously met. | Substantially changed. The 6th and 7th Plan used measures as described in the RW Beck Study ("Northwest Energy Efficiency Alliance Distribution Efficiency Initiative Project Final Report.", December 2007). The 2021 Plan is a fresh approach which recognizes that "grid mod" (bringing switch gear into the existing system and adding new SCADA connected devices + AMI) can be leveraged once in place to enable more effective DEI/CVR from both a cost (since grid mod equipment can be used with CVR without cost attribution if already in place for other purposes) and implementation perspective (since a more connected distribution system is easier to leverage for other purposes). The need for grid mod to lead (rather than lag) for the the cost attribution savings to be realized for CVR is reflected in the ramp rate, which is paced more slowly initially to allow for ongoing grid mod work to be completed.
Energy Savings Calculation Basis | [kWh Sales] * [Sales Applicability by Class] * [CVRf] * [%DeltaV] Caluculations are done by utility and by measure. |  | In the past, the CVRf were taken from RW Beck Pilot data when known (limited #), and roughly estimated when not known (most). Given that these factors are very system dependent and can change over time depending on the voltage loading profile, the 2021 Plan uses a different approach of selecting a base CVRf based on collaboration with BPA and a lit review, and modifies that based on the heating and cooling zone where a utility is located given how substantially HVAC contributes to Res + Commercial sales. As a check, staff looked the Smart Grid reports filed with the PUCs where CVR was tested more recently by several IOUs and found the numbers here to be generally in range, again recognizing that CVR factors on one feeder at one utility (as published in a Smart Grid Report) may be different than CVR Factors across the entire system, especially given that CVR factors are closely tied with the starting voltage, where systems which have a higher initial voltage would tend to see larger CVR factors. This is described in more detail on the Input Data sheet.
Baseline Energy Use | Utility specific from the 2018 Sales
Applicable Stock | Applicability ranges 5% to 85% of sales based on customer class.
Baseline Saturation | As estimated in RW Beck study with updates for completed projects. |  | Updates for completed projects thru 2018
Baseline Penetration | Adjusted remaining potential after interviews with system owners operators. | Utilities already doing LDC were deemed to have no potential for ECM1, but were still available for ECM2 and ECM3. The one note here is that even utilities doing LDC may not be doing it for CVR and could actually be eligible for ECM1 savings, so the approach taken in this workbook is conservative.
Permutations | None
Costs | Developed with the input of BPA | ECM1 Cost = the cost shown under ECM1 ECM2 Cost = ECM1 Cost + the cost shown under ECM2 ECM3 Cost = ECM2 Cost + the cost shown under ECM3 | Previous plan used very aggregated, substation level cost. The new approach used a bottoms up component cost.
Measure Life | 15 Years | RW Beck Study + Conversations with Utitliy Staff
Savings Shape | 8760 DEI shape created from RW Beck study data | S-All-UD-CVR-All-All-N
Achievability Ramp Rate | Retro1Slow, 100% Achievable | Slow ramp, full achievability. Ramp relects slower roll out of Grid Mod and AMI. Achievability; While a retrofit measure, its not subject to end-user acceptance. It’s a utility decision. | Revised to align with slower roll out of Grid Mod and AMI
Narrative Description of DEI for the 2021 Plan In brief summary, the Council develops an EE supply curve for CVR across the region. In the last two plans the Council approach has used data from an RW-Beck/NEEA study where CVR was piloted back in 2007. The study produced utility specific maximum dVoltage (%) along with utility specific CVR factors (dPower/dVoltage) and (generic) estimated costs on a per substation basis. The past approach built up the CVR supply curve using three “levels” of distribution efficiency upgrades. The first was simple LDC with no feedback. The next was LDC with mild system upgrades (phase load balancing, etc.). The third was a variable LDC factor with end of line measurement input, plus moderate system upgrades (mid-line VRs, reconductoring, etc.). This created a supply curve with monotonically increasing costs. In this plan, the goal was to refresh CVR factors (given LED lights and other inverter-based constant power devices) and incorporate the benefit of existing AMI in building up the supply curve. The challenge with considering AMI is cost attribution for upgrades related to CVR. Let’s say you have LDC on a feeder now, and you want to use some off the shelf software (like DVI’s Edge product) to change the LDC settings based on feedback from bellwether AMI connected meters. You’ll likely have to bring in SCADA to tie in your tap changers, but at the same time, SCADA connecting tap changers is also a best practice for safety, so how should costs be attributed? Should it just be the cost of the software + IT staff to keep it running? Then at the same time, how do we know who already is doing LDC, and to what extent? How can we generalize this to a regional level? To address these questions and build up the 2021 Plan Supply Curve, Mike worked with distribution engineers at regional IOUs and Publics. To majority view (albeit not neccesarilly always concensus) from those conversations were: 1) Utilities are making substantial grid modernization investments, and CVR may be a great way to capture some benefit from them beyond traditional SAIDI/SAIFI interruption metrics. 2) CVR through LDC is done by some utilities already, but unlike typical conservation measures that have a program history and expectation of execution, DEI is likely to fall under the radar without a push. If it isn't a norm for the distribution team, and there isn't a push from managment or standards, incentives falter. 3) While AMI might be lower cost for larger utilities that have the bandwidth to manage the program, for medium to small utilities the burden of the IT load on implementation and maintence could be prohibitive until Smart Grid is more well developed. Right now data just isn't well collected, processed, and integrated in many places. The good news here is that DEI has an aquisition ramp rate, so we can take that into account there without impacting the supply curve itself. Takeaway Conclusions: - CVR w/ AMI likely very workable with AMI installed in last ~10 years (2010 or more recent), including Power Line Carrier (although some may debate PLC being sufficient). Older AMI may not have the quality needed. While bandwidth can be an issue, in general for bellwether AMI, you may need ~10-20 per voltage controlled device, so a substation serving 2k customers could need telemetry from just 10-20 meters. "Existing AMI" could be limited to only utilities who have added it in the last 10 years, however utilities with much older equipment may well refresh it by the time the ramp rate catches up. - CVR w/ AMI probably not workable for utilities with less than 35,000 customers without some sort of consulting services team to help support it from BPA or etc. The initial data setup to pull in AMI data, configure the system, etc. is likely just too high for a smaller engineering and IT team and utilities these size. We could limit CVR w/ AMI to utilities w/ >35k customers, however at the same time, this actually could be a key area for BPA and is a role they are trying to take on. - CVR w/ AMI needs to remotely control voltage settings and while it may not require SCADA (could be some other form of OTA communication), this is very case by case and not an approachable path to work down for this regional potential work. Instead, the DEI ramp rate will be at a pace where it it will follow (not lead) grid mod around the region. This will allow the costs for CVR w/ AMI to really be on the software/implementation/IT side, not the hardware side (that is mostly getting upgraded, anyway)

## 7P to 8P
Measure-Specific Updates and Changes
Item | Description | Note
1 | Convert to 8P format and links | Grist 11/23/2019
2 | Revise forRPM to link to new M_Input_Out format and reformat for 2021P ship to RPM | Grist 11/23/2019
3 | Updated and linked DE_Master | Grist 11/23/2019
4 | Revised measure header on M_Input to 8P format | Grist 11/23/2019
5 | Run on ProCost to check functionality | Grist 11/23/2019: It worked after some clean up of linked files
6 | Updated SC Retro for forecast, MAX achievable, and housekeeping | Grist 11/23/2019
7 | Moved some early-version files to the Bone Yard | Grist 11/23/2019
8 | Talk to Mike about Ramp Rates [MS] I think Retro1Slow is the best fit, but am also comfortable w/ continuing w/ Retro3Slow.
9 | Talk to Mike about the logic for interaction with other savings | Applies to new systems as well as old
10 | O&M vs. measure life. Can consider doing periodic O&M (instead of yearly) - columns 9 - 14 of M_input | MS 1/29/2020: O&M methodology is set up to take detailed data from utility managers, if/when available. Assuming 5% across the board for now.
11 | Need to remove "achieved" energy potential as per 7P. Low priority as it is only ~50k MWh.
12 | Think about measure life. | MS 1/29/2020: Confirmed 15 year measure life is reasonabl
13 | When all complete, update final few fields of source summary
14 | Build in ECM1 switch to set to zero for utilities who feel they are doing LDC well | MS 1/31/2020 Added Jan 29, column J
15 | Double w/ CG check how we normally limit to 85% achievability | MS/CG It’s a utility decision, not a consumer decision - go to 100%
16 | Figure out incrementality because ECM# is lower cost than ECM2 | 1/31/2020 MS/CG Combine ECM2 and ECM3
17 | Add BPA split | MS 1/29/2020 Drop Down on RollUp in B2
18 | Address review comments | 2020-04-02
19 | Revise to remove duplicate "Delivery" sales and "Power Marketer" sales | 2020-04-10
20 | Revise to add BPA sales not reported to EIA | 2020-04-10
21 | Revise to link to final draft forecast and update with new estimate of conservation EE interaction | 2020-04-14
22
23 | Run with BPA Split
24 | Update with Final Plan Frozen Efficiency Forecast and Conservation
25 | Re-Run to generate final forRPM
26
27
How to Update 7P Workbook to 2021P Format
Item | Description | Note
1 | Start with 7P sheet
2 | Move to 8P folder in Q
3 | Revise name | Format: Com-MeasureName-2021P_Vx
4 | Color all sheets orange as a signal that sheet needs update for 8P | Clear orange color when updated
5 | Update links to 8P datasets. Import and revise link files if needed. | Links are in "File" option.
6 | Link workbook to ComMaster | Column C
7 | Review methodology and update or change if needed
8 | Update baseline assumptions
9 | Calibrate turnover-induced load forecast with Massoud. | Check frozen baseline forecast and calibrate implied CPA baseline
10 | Revise link in SC worksheets to correct measure name in ComMaster (measure name & plan date range linked) | Cell C8 in SC curves links to ComMaster or Source Summary by measure name
11 | Revise "Achievable per Year" SC to eliminate annual MAX.
12 | Check SC sheets for proper application of Max | Can be other than 85%
13 | Check measure bundle name in SC sheets | Lookup from ComMaster or SC sheets
14 | Build or Update measure costs and savings inputs
15 | Update to 2016$
16 | Identify appropriate savings profile or make new one. Update profile in GLS if needed. | GLS are in "Conservation Data Files" in Q Drive
17 | Add new ProCost measure input header | New header set, 19 columns, remove LO Retro, Header set next sheet
18 | Link costs and savings to new ProCost input format
19 | Run ProCost in Batch Runner | Use Commercial settings for Global. Use current version ProCost:
20 | Select appropriate bundling of measures for supply curve builder
21 | Link output matrix to appropriate slot in SC worksheets and forRPM | M_Input_Output, extend named range MeasOut to column AN
22 | Review SC Ramp Rates. Select appropriate or make new.
23 | Verify MAX is working correctly with Ramp Rate methodology
24 | Build forRPM: Move worksheet to left at second position
25 | Build forRPM: Add column for Peak 2 | Add Peak 2, Insert at column G, change headers
26 | Build forRPM: Check links on forRPM sheet to make sure columns match new M_Input_Out | Check Name references, Offset years (-10), Year header linked, offset shape (-17), Extend MeasOut to col AN.
27 | Update 2021PSource Summary and as install lleft-most sheet
28 | Update LOG
29 | Delete old sheets no longer used

## forRPM
Ramp Rate | Resource Type | Measure Category | Sector | End Use | kW per unit1 | kW per unit2 | kWh per unit | TRC Net Levelized Cost (Net of All Benefits) | segment | measure | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | MAX | Savings Allocation by Category and Month for Segments 1 | [11 empty] | Savings Allocation by Category and Month for Segments 2
[5 empty] | Wholesale KW | Wholesale KW | Busbar Savings | lvlcost |  |  | aMW_2022 | aMW_2023 | aMW_2024 | aMW_2025 | aMW_2026 | aMW_2027 | aMW_2028 | aMW_2029 | aMW_2030 | aMW_2031 | aMW_2032 | aMW_2033 | aMW_2034 | aMW_2035 | aMW_2036 | aMW_2037 | aMW_2038 | aMW_2039 | aMW_2040 | aMW_2041 | MAX | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | TRC B/C
Retro1Slow | Retro | Utility Distribution System | Utility | Utility Distribution Sytem | 0.00022522 | 0.00023795 | 1.7102 | 23.3135 | Utility System | EMC-1 LDC with no VVO | 0.096223 | 0.18994 | 0.33523 | 0.54368 | 0.80791 | 1.1706 | 1.5685 | 1.9852 | 2.4132 | 2.8519 | 3.2296 | 3.3427 | 3.3982 | 3.2276 | 2.8079 | 2.2689 | 1.7512 | 1.1957 | 0.7754 | 0.50783 | 29.2973 | 0.027192 | 0.025269 | 0.028944 | 0.016197 | 0.016045 | 0.016207 | 0.027602 | 0.028628 | 0.026461 | 0.024516 | 0.022137 | 0.028267 | 0.13911 | 0.12389 | 0.135 | 0.1008 | 0.10447 | 0.10083 | 0.12236 | 0.12101 | 0.1175 | 0.11021 | 0.10967 | 0.13785 | 1.3091
Retro1Slow | Retro | Utility Distribution System | Utility | Utility Distribution Sytem | 0.0012708 | 0.0012708 | 9.1332 | 55.3102 | Utility System | ECM-2 & ECM-3 LDC with VVO & AMI | 0.51388 | 1.0144 | 1.7903 | 2.9035 | 4.3147 | 6.2514 | 8.3764 | 10.602 | 12.8881 | 15.2305 | 17.2477 | 17.8518 | 18.1484 | 17.2374 | 14.9959 | 12.1172 | 9.3523 | 6.3856 | 4.141 | 2.7121 | 156.4635 | 0.14522 | 0.13495 | 0.15458 | 0.086502 | 0.085689 | 0.086555 | 0.14741 | 0.15289 | 0.14132 | 0.13093 | 0.11822 | 0.15096 | 0.74292 | 0.66162 | 0.72098 | 0.53834 | 0.55791 | 0.53848 | 0.65348 | 0.64623 | 0.62751 | 0.58856 | 0.58571 | 0.7362 | 0.5696
Note on A1: Charlie Grist: Lookup in ComMaster
Note on B1: Charlie Grist: New, NR, Retro
Note on C1: Charlie Grist: Measure Index Name
Note on E1: Charlie Grist: Use Massoud's Names
Note on F1: Charlie Grist: From Shaped Savings column 14
Note on G1: Charlie Grist: From Shaped Savings column 15
Note on H1: Charlie Grist: From SC or from Shaped Savings column 3.
Note on I1: Charlie Grist: From SC or from Shaped Savings column K (column 11)
Note on J1: Charlie Grist: From SC
Note on K1: Charlie Grist: From SC
Note on L1: Charlie Grist: From SC
Note on AG1: Charlie Grist: From Shaped Savings. Copy whole row down since column increment is hardwired into formula.

## SC-Retro
Units Methodology | Savings are based on end system sales. MWh savings per MWh system sales.
Forecast Version
| Vintage | Retro | Stock
End-Use: | Measure Bundle | Utility Distribution System | Region
Utility Distribution System | Report Year | 2041 | Base
| Total Potential (aMW) | 185.7608 |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
UNITS FOR EXISTING STOCK |  |  |  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | MAX | TOTAL
|  |  |  | FLOOR_2022 | FLOOR_2023 | FLOOR_2024 | FLOOR_2025 | FLOOR_2026 | FLOOR_2027 | FLOOR_2028 | FLOOR_2029 | FLOOR_2030 | FLOOR_2031 | FLOOR_2032 | FLOOR_2033 | FLOOR_2034 | FLOOR_2035 | FLOOR_2036 | FLOOR_2037 | FLOOR_2038 | FLOOR_2039 | FLOOR_2040 | FLOOR_2041 | 85%
|  | TotalLoad | Update with Final Plan Frozen Efficiency Forecast | 22058.6529 | 21921.1062 | 21951.0538 | 22069.3296 | 21824.3607 | 22295.9612 | 22211.9613 | 21960.249 | 21862.63 | 22156.3814 | 22580.1779 | 22252.772 | 22701.1863 | 23033.2261 | 22990.8147 | 22695.8617 | 23033.2207 | 22911.5822 | 23337.7867 | 23517.6264
|  | Frozen Efficiency Sales in MWh |  | 193233799.404 | 192028890.312 | 192291231.288 | 193327327.296 | 191181399.732 | 195312620.112 | 194576780.988 | 192371781.24 | 191516638.8 | 194089901.064 | 197802358.404 | 194934282.72 | 198862391.988 | 201771060.636 | 201399536.772 | 198815748.492 | 201771013.332 | 200705460.072 | 204439011.492 | 206014407.264
|  | Forecast After Conservation |  | 192203461.5605 | 189799774.9429 | 188668040.5158 | 188106842.5492 | 184159604.898 | 186301924.1248 | 183513913.6053 | 179173047.0302 | 176101235.1959 | 176476729.3407 | 178129701.2682 | 173309933.6681 | 175456923.0792 | 176784364.3441 | 174922796.9965 | 170912692.3075 | 172502689.1483 | 170130349.6588 | 172688810.9997 | 173419806.7904
|  |  |  | 117.6185 | 254.4652 | 413.6063 | 595.9457 | 801.5748 | 1028.6183 | 1262.8844 | 1506.7048 | 1759.7493 | 2010.636 | 2245.7371 | 2468.533 | 2671.8572 | 2852.3626 | 3022.4589 | 3185.2804 | 3341.1329 | 3490.3094 | 3624.4521 | 3720.8448
|  |  | Placeholder EE by Load Case | 117.6185 | 136.8467 | 159.141 | 182.3395 | 205.629 | 227.0435 | 234.2661 | 243.8204 | 253.0445 | 250.8868 | 235.1011 | 222.7959 | 203.3242 | 180.5054 | 170.0963 | 162.8215 | 155.8525 | 149.1765 | 134.1427 | 96.3927
|  |  | Placeholder Conservation in aMW - from draft supply curves at $100/MWh | 117.6185 | 136.8467 | 159.141 | 182.3395 | 205.629 | 227.0435 | 234.2661 | 243.8204 | 253.0445 | 250.8868 | 235.1011 | 222.7959 | 203.3242 | 180.5054 | 170.0963 | 162.8215 | 155.8525 | 149.1765 | 134.1427 | 96.3927
|  |  | High to Base ratio | 0.63355 | 0.637 | 0.64051 | 0.64512 | 0.64881 | 0.65283 | 0.65562 | 0.6582 | 0.66091 | 0.66366 | 0.66595 | 0.66755 | 0.67016 | 0.67158 | 0.67357 | 0.67658 | 0.68014 | 0.68254 | 0.68562 | 0.68744 | 0.68973
|  |  | Low to Base ratio | 0.60291 | 0.59949 | 0.59614 | 0.5928 | 0.5895 | 0.58592 | 0.58372 | 0.58089 | 0.57766 | 0.57503 | 0.57315 | 0.57178 | 0.56908 | 0.56772 | 0.56608 | 0.56328 | 0.56027 | 0.55902 | 0.55691 | 0.55627 | 0.55499
|  |  | Achievability | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041
Incremental based on achievability, ramp rate, and applicability |  | Utility Distribution System | Retro1Slow | 0.2564% | 0.5126% | 0.9102% | 1.48% | 2.247% | 3.218% | 4.378% | 5.675% | 7.02% | 8.278% | 9.287% | 9.88% | 9.921% | 9.352% | 8.223% | 6.8% | 5.2% | 3.6% | 2.3% | 1.5%
Applicability in RegionWideSubstations |  |  |  | 492885.995 | 972925.3291 | 1717172.4376 | 2784907.8333 | 4138399.5442 | 5996021.7601 | 8034178.0591 | 10168833.8314 | 12361468.3049 | 14608189.8431 | 16542951.5828 | 17122409.78 | 17406894.1069 | 16533077.1429 | 14383203.2872 | 11622063.0769 | 8970139.8357 | 6124692.5877 | 3971842.653 | 2601297.1019 | 150070520.9787 | 176553554.0925
Acheivable Per Year
SUPPLY CURVE SAVINGS BY BUNDLE |  | Utility Distribution System |  | 2022: aMW
|  |  |  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | TOTAL MAX | TOTAL
Busbar Savings (kWh) | lvlcost | segment | measure | aMW_2022 | aMW_2023 | aMW_2024 | aMW_2025 | aMW_2026 | aMW_2027 | aMW_2028 | aMW_2029 | aMW_2030 | aMW_2031 | aMW_2032 | aMW_2033 | aMW_2034 | aMW_2035 | aMW_2036 | aMW_2037 | aMW_2038 | aMW_2039 | aMW_2040 | aMW_2041 | TOTAL MAX | TOTAL
1.7102 | 23.3135 |  | EMC-1 LDC with no VVO | 0.096223 | 0.18994 | 0.33523 | 0.54368 | 0.80791 | 1.1706 | 1.5685 | 1.9852 | 2.4132 | 2.8519 | 3.2296 | 3.3427 | 3.3982 | 3.2276 | 2.8079 | 2.2689 | 1.7512 | 1.1957 | 0.7754 | 0.50783 | 29.2973 | 34.4674
9.1332 | 55.3102 |  | ECM-2 & ECM-3 LDC with VVO & AMI | 0.51388 | 1.0144 | 1.7903 | 2.9035 | 4.3147 | 6.2514 | 8.3764 | 10.602 | 12.8881 | 15.2305 | 17.2477 | 17.8518 | 18.1484 | 17.2374 | 14.9959 | 12.1172 | 9.3523 | 6.3856 | 4.141 | 2.7121 | 156.4635 | 184.0747
|  |  |  | 0.61011 | 1.2043 | 2.1256 | 3.4472 | 5.1226 | 7.422 | 9.9449 | 12.5872 | 15.3013 | 18.0824 | 20.4772 | 21.1945 | 21.5467 | 20.465 | 17.8039 | 14.3861 | 11.1034 | 7.5813 | 4.9164 | 3.2199 | 185.7608 | 218.5421
RECOMBINE MEASURE BUNDLES INTO SUPPLY CURVE CUMULATIVE
|  |  |  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | Max
|  | lvlcost | lvlcost | aMW_2022 | aMW_2023 | aMW_2024 | aMW_2025 | aMW_2026 | aMW_2027 | aMW_2028 | aMW_2029 | aMW_2030 | aMW_2031 | aMW_2032 | aMW_2033 | aMW_2034 | aMW_2035 | aMW_2036 | aMW_2037 | aMW_2038 | aMW_2039 | aMW_2040 | aMW_2041 | max
| Block 1: <= 0 mills/kWh | >=-9999 | <=0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 2: <= 10 mills/kWh | >0 | <=10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 3: 10-20 mills/kWh | >10 | <=20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 4: 20-30 mills/kWh | >20 | <=30 | 0.096223 | 0.18994 | 0.33523 | 0.54368 | 0.80791 | 1.1706 | 1.5685 | 1.9852 | 2.4132 | 2.8519 | 3.2296 | 3.3427 | 3.3982 | 3.2276 | 2.8079 | 2.2689 | 1.7512 | 1.1957 | 0.7754 | 0.50783 | 29.2973
| Block 5: 30-40 mills/kWh | >30 | <=40 | 0.096223 | 0.18994 | 0.33523 | 0.54368 | 0.80791 | 1.1706 | 1.5685 | 1.9852 | 2.4132 | 2.8519 | 3.2296 | 3.3427 | 3.3982 | 3.2276 | 2.8079 | 2.2689 | 1.7512 | 1.1957 | 0.7754 | 0.50783 | 29.2973
| Block 6: 40-50 mills/kWh | >40 | <=50 | 0.096223 | 0.18994 | 0.33523 | 0.54368 | 0.80791 | 1.1706 | 1.5685 | 1.9852 | 2.4132 | 2.8519 | 3.2296 | 3.3427 | 3.3982 | 3.2276 | 2.8079 | 2.2689 | 1.7512 | 1.1957 | 0.7754 | 0.50783 | 29.2973
| Block 7: 50-60 mills/kWh | >50 | <=60 | 0.61011 | 1.2043 | 2.1256 | 3.4472 | 5.1226 | 7.422 | 9.9449 | 12.5872 | 15.3013 | 18.0824 | 20.4772 | 21.1945 | 21.5467 | 20.465 | 17.8039 | 14.3861 | 11.1034 | 7.5813 | 4.9164 | 3.2199 | 185.7608
| Block 8: 60-70 mills/kWh | >60 | <=70 | 0.61011 | 1.2043 | 2.1256 | 3.4472 | 5.1226 | 7.422 | 9.9449 | 12.5872 | 15.3013 | 18.0824 | 20.4772 | 21.1945 | 21.5467 | 20.465 | 17.8039 | 14.3861 | 11.1034 | 7.5813 | 4.9164 | 3.2199 | 185.7608
| Block 9: 70-80 mills/kWh | >70 | <=80 | 0.61011 | 1.2043 | 2.1256 | 3.4472 | 5.1226 | 7.422 | 9.9449 | 12.5872 | 15.3013 | 18.0824 | 20.4772 | 21.1945 | 21.5467 | 20.465 | 17.8039 | 14.3861 | 11.1034 | 7.5813 | 4.9164 | 3.2199 | 185.7608
| Block 10: 80-90 mills/kWh | >80 | <=90 | 0.61011 | 1.2043 | 2.1256 | 3.4472 | 5.1226 | 7.422 | 9.9449 | 12.5872 | 15.3013 | 18.0824 | 20.4772 | 21.1945 | 21.5467 | 20.465 | 17.8039 | 14.3861 | 11.1034 | 7.5813 | 4.9164 | 3.2199 | 185.7608
| Block 11: 90-100 mills/kWh | >90 | <=100 | 0.61011 | 1.2043 | 2.1256 | 3.4472 | 5.1226 | 7.422 | 9.9449 | 12.5872 | 15.3013 | 18.0824 | 20.4772 | 21.1945 | 21.5467 | 20.465 | 17.8039 | 14.3861 | 11.1034 | 7.5813 | 4.9164 | 3.2199 | 185.7608
| Block 12: 100-110 mills/kWh | >100 | <=110 | 0.61011 | 1.2043 | 2.1256 | 3.4472 | 5.1226 | 7.422 | 9.9449 | 12.5872 | 15.3013 | 18.0824 | 20.4772 | 21.1945 | 21.5467 | 20.465 | 17.8039 | 14.3861 | 11.1034 | 7.5813 | 4.9164 | 3.2199 | 185.7608
| Block 13: 110-120 mills/kWh | >110 | <=120 | 0.61011 | 1.2043 | 2.1256 | 3.4472 | 5.1226 | 7.422 | 9.9449 | 12.5872 | 15.3013 | 18.0824 | 20.4772 | 21.1945 | 21.5467 | 20.465 | 17.8039 | 14.3861 | 11.1034 | 7.5813 | 4.9164 | 3.2199 | 185.7608
| Block 14: 120-130 mills/kWh | >120 | <=130 | 0.61011 | 1.2043 | 2.1256 | 3.4472 | 5.1226 | 7.422 | 9.9449 | 12.5872 | 15.3013 | 18.0824 | 20.4772 | 21.1945 | 21.5467 | 20.465 | 17.8039 | 14.3861 | 11.1034 | 7.5813 | 4.9164 | 3.2199 | 185.7608
| Block 15: 130-140 mills/kWh | >130 | <=140 | 0.61011 | 1.2043 | 2.1256 | 3.4472 | 5.1226 | 7.422 | 9.9449 | 12.5872 | 15.3013 | 18.0824 | 20.4772 | 21.1945 | 21.5467 | 20.465 | 17.8039 | 14.3861 | 11.1034 | 7.5813 | 4.9164 | 3.2199 | 185.7608
| Block 16: 140-150 mills/kWh | >140 | <=150 | 0.61011 | 1.2043 | 2.1256 | 3.4472 | 5.1226 | 7.422 | 9.9449 | 12.5872 | 15.3013 | 18.0824 | 20.4772 | 21.1945 | 21.5467 | 20.465 | 17.8039 | 14.3861 | 11.1034 | 7.5813 | 4.9164 | 3.2199 | 185.7608
| Block 17: 150-160 mills/kWh | >150 | <=160 | 0.61011 | 1.2043 | 2.1256 | 3.4472 | 5.1226 | 7.422 | 9.9449 | 12.5872 | 15.3013 | 18.0824 | 20.4772 | 21.1945 | 21.5467 | 20.465 | 17.8039 | 14.3861 | 11.1034 | 7.5813 | 4.9164 | 3.2199 | 185.7608
| Block 18: 160-170 mills/kWh | >160 | <=170 | 0.61011 | 1.2043 | 2.1256 | 3.4472 | 5.1226 | 7.422 | 9.9449 | 12.5872 | 15.3013 | 18.0824 | 20.4772 | 21.1945 | 21.5467 | 20.465 | 17.8039 | 14.3861 | 11.1034 | 7.5813 | 4.9164 | 3.2199 | 185.7608
| Block 19: 170-180 mills/kWh | >170 | <=180 | 0.61011 | 1.2043 | 2.1256 | 3.4472 | 5.1226 | 7.422 | 9.9449 | 12.5872 | 15.3013 | 18.0824 | 20.4772 | 21.1945 | 21.5467 | 20.465 | 17.8039 | 14.3861 | 11.1034 | 7.5813 | 4.9164 | 3.2199 | 185.7608
| Block 20: 180-190 mills/kWh | >180 | <=190 | 0.61011 | 1.2043 | 2.1256 | 3.4472 | 5.1226 | 7.422 | 9.9449 | 12.5872 | 15.3013 | 18.0824 | 20.4772 | 21.1945 | 21.5467 | 20.465 | 17.8039 | 14.3861 | 11.1034 | 7.5813 | 4.9164 | 3.2199 | 185.7608
| Block 21: 190-200 mills/kWh | >190 | <=200 | 0.61011 | 1.2043 | 2.1256 | 3.4472 | 5.1226 | 7.422 | 9.9449 | 12.5872 | 15.3013 | 18.0824 | 20.4772 | 21.1945 | 21.5467 | 20.465 | 17.8039 | 14.3861 | 11.1034 | 7.5813 | 4.9164 | 3.2199 | 185.7608
| Block 22: 200-210 mills/kWh | >200 | <=210 | 0.61011 | 1.2043 | 2.1256 | 3.4472 | 5.1226 | 7.422 | 9.9449 | 12.5872 | 15.3013 | 18.0824 | 20.4772 | 21.1945 | 21.5467 | 20.465 | 17.8039 | 14.3861 | 11.1034 | 7.5813 | 4.9164 | 3.2199 | 185.7608
| Block 23: 210-220 mills/kWh | >210 | <=220 | 0.61011 | 1.2043 | 2.1256 | 3.4472 | 5.1226 | 7.422 | 9.9449 | 12.5872 | 15.3013 | 18.0824 | 20.4772 | 21.1945 | 21.5467 | 20.465 | 17.8039 | 14.3861 | 11.1034 | 7.5813 | 4.9164 | 3.2199 | 185.7608
| Block 24: 220-230 mills/kWh | >220 | <=230 | 0.61011 | 1.2043 | 2.1256 | 3.4472 | 5.1226 | 7.422 | 9.9449 | 12.5872 | 15.3013 | 18.0824 | 20.4772 | 21.1945 | 21.5467 | 20.465 | 17.8039 | 14.3861 | 11.1034 | 7.5813 | 4.9164 | 3.2199 | 185.7608
| Block 25: 230-240 mills/kWh | >230 | <=240 | 0.61011 | 1.2043 | 2.1256 | 3.4472 | 5.1226 | 7.422 | 9.9449 | 12.5872 | 15.3013 | 18.0824 | 20.4772 | 21.1945 | 21.5467 | 20.465 | 17.8039 | 14.3861 | 11.1034 | 7.5813 | 4.9164 | 3.2199 | 185.7608
| Block 26: 240-250 mills/kWh | >240 | <=250 | 0.61011 | 1.2043 | 2.1256 | 3.4472 | 5.1226 | 7.422 | 9.9449 | 12.5872 | 15.3013 | 18.0824 | 20.4772 | 21.1945 | 21.5467 | 20.465 | 17.8039 | 14.3861 | 11.1034 | 7.5813 | 4.9164 | 3.2199 | 185.7608
| Block 27: 250-260 mills/kWh | >250 | <=260 | 0.61011 | 1.2043 | 2.1256 | 3.4472 | 5.1226 | 7.422 | 9.9449 | 12.5872 | 15.3013 | 18.0824 | 20.4772 | 21.1945 | 21.5467 | 20.465 | 17.8039 | 14.3861 | 11.1034 | 7.5813 | 4.9164 | 3.2199 | 185.7608
| Block 28: 260-270 mills/kWh | >260 | <=270 | 0.61011 | 1.2043 | 2.1256 | 3.4472 | 5.1226 | 7.422 | 9.9449 | 12.5872 | 15.3013 | 18.0824 | 20.4772 | 21.1945 | 21.5467 | 20.465 | 17.8039 | 14.3861 | 11.1034 | 7.5813 | 4.9164 | 3.2199 | 185.7608
| Block 29: 270-280 mills/kWh | >270 | <=280 | 0.61011 | 1.2043 | 2.1256 | 3.4472 | 5.1226 | 7.422 | 9.9449 | 12.5872 | 15.3013 | 18.0824 | 20.4772 | 21.1945 | 21.5467 | 20.465 | 17.8039 | 14.3861 | 11.1034 | 7.5813 | 4.9164 | 3.2199 | 185.7608
| Block 30: 280-290 mills/kWh | >280 | <=290 | 0.61011 | 1.2043 | 2.1256 | 3.4472 | 5.1226 | 7.422 | 9.9449 | 12.5872 | 15.3013 | 18.0824 | 20.4772 | 21.1945 | 21.5467 | 20.465 | 17.8039 | 14.3861 | 11.1034 | 7.5813 | 4.9164 | 3.2199 | 185.7608
| Block 31: 290-300 mills/kWh | >290 | <=300 | 0.61011 | 1.2043 | 2.1256 | 3.4472 | 5.1226 | 7.422 | 9.9449 | 12.5872 | 15.3013 | 18.0824 | 20.4772 | 21.1945 | 21.5467 | 20.465 | 17.8039 | 14.3861 | 11.1034 | 7.5813 | 4.9164 | 3.2199 | 185.7608
| Block 32: >300 mills/kWh | >300 | <=999 | 0.61011 | 1.2043 | 2.1256 | 3.4472 | 5.1226 | 7.422 | 9.9449 | 12.5872 | 15.3013 | 18.0824 | 20.4772 | 21.1945 | 21.5467 | 20.465 | 17.8039 | 14.3861 | 11.1034 | 7.5813 | 4.9164 | 3.2199 | 185.7608
|  |  |  | 0.61011 | 1.2043 | 2.1256 | 3.4472 | 5.1226 | 7.422 | 9.9449 | 12.5872 | 15.3013 | 18.0824 | 20.4772 | 21.1945 | 21.5467 | 20.465 | 17.8039 | 14.3861 | 11.1034 | 7.5813 | 4.9164 | 3.2199 | 185.7608
RECOMBINE MEASURE BUNDLES INTO SUPPLY CURVE INCREMENTAL
|  |  | Utility Distribution System | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | Max
|  |  |  | aMW_2022 | aMW_2023 | aMW_2024 | aMW_2025 | aMW_2026 | aMW_2027 | aMW_2028 | aMW_2029 | aMW_2030 | aMW_2031 | aMW_2032 | aMW_2033 | aMW_2034 | aMW_2035 | aMW_2036 | aMW_2037 | aMW_2038 | aMW_2039 | aMW_2040 | aMW_2041 | aMW_MAX
|  | Block 1: <= 0 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 2: <= 10 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 3: 10-20 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 4: 20-30 mills/kWh |  | 0.096223 | 0.18994 | 0.33523 | 0.54368 | 0.80791 | 1.1706 | 1.5685 | 1.9852 | 2.4132 | 2.8519 | 3.2296 | 3.3427 | 3.3982 | 3.2276 | 2.8079 | 2.2689 | 1.7512 | 1.1957 | 0.7754 | 0.50783 | 29.2973
|  | Block 5: 30-40 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 6: 40-50 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 7: 50-60 mills/kWh |  | 0.51388 | 1.0144 | 1.7903 | 2.9035 | 4.3147 | 6.2514 | 8.3764 | 10.602 | 12.8881 | 15.2305 | 17.2477 | 17.8518 | 18.1484 | 17.2374 | 14.9959 | 12.1172 | 9.3523 | 6.3856 | 4.141 | 2.7121 | 156.4635
|  | Block 8: 60-70 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 9: 70-80 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 10: 80-90 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 11: 90-100 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 12: 100-110 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 13: 110-120 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 14: 120-130 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 15: 130-140 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 16: 140-150 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 17: 150-160 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 18: 160-170 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 19: 170-180 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 20: 180-190 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 21: 190-200 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 22: 200-210 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 23: 210-220 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 24: 220-230 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 25: 230-240 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 26: 240-250 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 27: 250-260 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 28: 260-270 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 29: 270-280 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 30: 280-290 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 31: 290-300 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Block 32: >300 mills/kWh |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Total per Year |  | 0.61011 | 1.2043 | 2.1256 | 3.4472 | 5.1226 | 7.422 | 9.9449 | 12.5872 | 15.3013 | 18.0824 | 20.4772 | 21.1945 | 21.5467 | 20.465 | 17.8039 | 14.3861 | 11.1034 | 7.5813 | 4.9164 | 3.2199 | TOTAL MAX | TOTAL
|  | Total Cumulative |  | 0.61011 | 1.8144 | 3.94 | 7.3872 | 12.5098 | 19.9318 | 29.8767 | 42.4639 | 57.7652 | 75.8476 | 96.3248 | 117.5194 | 139.066 | 159.531 | 177.3349 | 185.7608 | 185.7608 | 185.7608 | 185.7608 | 185.7608 | 185.7608 | 218.5421
|  | Ramp Rate | Retro1Slow | 0.61011 | 1.2043 | 2.1256 | 3.4472 | 5.1226 | 7.422 | 9.9449 | 12.5872 | 15.3013 | 18.0824 | 20.4772 | 21.1945 | 21.5467 | 20.465 | 17.8039 | 14.3861 | 11.1034 | 7.5813 | 4.9164 | 3.2199 | TOTAL MAX
|  | Ramp Rate - Cumulative | Retro1Slow | 0.61011 | 1.8144 | 3.94 | 7.3872 | 12.5098 | 19.9318 | 29.8767 | 42.4639 | 57.7652 | 75.8476 | 96.3248 | 117.5194 | 139.066 | 159.531 | 177.3349 | 185.7608 | 185.7608 | 185.7608 | 185.7608 | 185.7608 | 185.7608
|  | Total per Year | 7P Final with 8P Sales forecast | 2.1368 | 3.4364 | 4.7492 | 6.5093 | 7.633 | 8.7681 | 9.9145 | 10.6296 | 11.3517 | 12.0809 | 12.8173 | 13.561 | 13.6303 | 13.7 | 13.7701 | 13.8406 | 13.9114 | 13.9825 | 14.054 | 14.1259
|  | Total Cumulative |  | 2.1368 | 5.5732 | 10.3224 | 16.8316 | 24.4647 | 33.2327 | 43.1473 | 53.7769 | 65.1286 | 77.2095 | 90.0269 | 103.5878 | 117.2181 | 130.9182 | 144.6883 | 158.5289 | 172.4402 | 186.4227 | 200.4768 | 214.6027 | 214.6027
|  | Busbar Savings (kWh) | lvlcost
|  | 4.4347 | -27.3396
|  | 2.6564 | -21.5086
|  | 2.9179 | 34.7339
|  | 1.4954 | 71.421
|  |  | V4 | 0.55649 | 1.1172 | 1.9938 | 3.2598 | 4.9732 | 7.1592 | 9.7883 | 12.754 | 15.8552 | 18.7927 | 21.1921 | 22.6597 | 22.8707 | 21.6698 | 19.15 | 15.6682 | 11.7711 | 8.0464 | 4.955 | 2.3891 | TOTAL MAX
|  |  | V4 | 0.55649 | 1.6737 | 3.6675 | 6.9273 | 11.9006 | 19.0598 | 28.848 | 41.6021 | 57.4573 | 76.25 | 97.4421 | 120.1018 | 142.9725 | 164.6423 | 183.7923 | 192.629 | 192.629 | 192.629 | 192.629 | 192.629 | 192.629
Note on C15: Charlie Grist: Represents sales after EE (excluding the EE from DE) to avoid over-counting savings potential of DE.
Note on D20: Charlie Grist: This adjusts the estimate of EE accomplished by High Base Low case
Note on D26: Charlie Grist: Link direct to Ramps. No lookup.
Note on Y12: Charlie Grist: Hard Coded here. Not linked to DE Master.

## M_Input_Out
Shaped Savings Results; By Category and sorted by TRC BC ratio
[15 empty] | Savings Allocation by Category and Month for Segments 1 | [11 empty] | Savings Allocation by Category and Month for Segments 2
Category | Measure | Busbar Savings | First Cost | Admin Cost | First Year Program Cost | PV Cost | PV Benefits | Unit Program Cost: First Year Program Cost in $/average annual kW saved | Utility System Net Levelized Cost (Net of T&D Capacity Benefits, Act Credit & Risk-Mitigation) in mills/kWh | TRC Net Levelized Cost (Net of All Benefits) in mills/kWh | TRC B/C Ratio | Net Electric & Gas System CO2 Avoided (Lifetime Tons) | Wholesale KW - Peak 1 | Wholesale KW - Peak 2 | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
EMC-1 LDC with no VVO |  | 1.7102 | 0.22989 | 0.045979 | 0.27587 | 0.47693 | 0.62434 | 1413.1113 | 23.3135 | 23.3135 | 1.3091 | 0.011928 | 0.00023795 | 0.00022522 | 0.027192 | 0.025269 | 0.028944 | 0.016197 | 0.016045 | 0.016207 | 0.027602 | 0.028628 | 0.026461 | 0.024516 | 0.022137 | 0.028267 | 0.13911 | 0.12389 | 0.135 | 0.1008 | 0.10447 | 0.10083 | 0.12236 | 0.12101 | 0.1175 | 0.11021 | 0.10967 | 0.13785
ECM-2 & ECM-3 LDC with VVO & AMI |  | 9.1332 | 3.3167 | 0.66334 | 3.98 | 5.8538 | 3.3343 | 3817.397 | 55.3102 | 55.3102 | 0.5696 | 0.063704 | 0.0012708 | 0.0012028 | 0.14522 | 0.13495 | 0.15458 | 0.086502 | 0.085689 | 0.086555 | 0.14741 | 0.15289 | 0.14132 | 0.13093 | 0.11822 | 0.15096 | 0.74292 | 0.66162 | 0.72098 | 0.53834 | 0.55791 | 0.53848 | 0.65348 | 0.64623 | 0.62751 | 0.58856 | 0.58571 | 0.7362

## M_input
Data Set Name
Measure Index Name | 0
Costs must be denominated in the same year as 'Input Cost Reference Year' = |  | 2016
See row 93 for inputs that results are based on | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23
Input Data | [7 empty] | Periodic Replacement Costs and Savings and Replacement Period | [5 empty] | Gas Inputs |  | Savings Period 2 Parameters (if applicable)
Measure Application | Savings Component | Savings for Period 1 (kwh/yr) | Measure Life (yrs) | Capital Cost | Annual O&M | Shape Pointer | Non-E Val ($/yr) | Cost A ($) | Replacement Period A (yrs) | Cost B ($) | Replacement Period B (yrs) | Cost C ($) | Replacement Period C (yrs) | Savings (therms/yr) | Shape Pointer | Savings for Period 2 (kWh/yr) | Length of Period 1 (yrs) | Base Case Cost at Start of Period 2 ($)
EMC-1 LDC with no VVO | 1 - LDC with no VVO | 1.5398 | 15 | 0.22989 | 0.017786 | S-All-UD-CVR-All-All-N
ECM-2 & ECM-3 LDC with VVO & AMI | 2 - LDC with VVO and EOL | 6.4047 | 15 | 3.2849 | 0.16424 | S-All-UD-CVR-All-All-N
ECM-2 & ECM-3 LDC with VVO & AMI | 3 - LDC with VVO and Existing AMI | 1.8187 | 15 | 0.031803 | 0.0015901 | S-All-UD-CVR-All-All-N
ProCost Results
Version: | ProCost 4.0.06
Run Time: | Sunday, 12 April , 2020 at 4:01 PM
Regurgitation of ProData input parameters which were used for this run
| Run Type: | Electric |  |  |  | Marginal Cost & Conservation Load Shape Parameters | [9 empty] | Sector: | Utility |  |  |  |  | Program Parameters |  |  | Utility System Parameters
| Negative B/C Ratios: | OFF: (Converts Negative B/C Ratios) |  |  |  | Marginal Costs and Savings Shape File | Q:\Eighth Plan\Conservation Analysis\ProCost v4\MC_AND_LOADSHAPE_v4.0.06.xlsx | [8 empty] | Sponsor Parameters | [5 empty] | Program Life (yrs) | 20 |  |  | Electric | Gas
| Admin Cost / Category Level: | ON: Admin Costs added at Measure Application Results |  |  |  | Marginal Elec Avoided Cost Input Worksheet | 2021P Electric Mid | [9 empty] | Customer | Wholesale Elec | Retail Elec | Nat Gas |  | Program Start Date | 2022 |  | Bulk System T&D Loss Factor | 0.023 | 0.01
| Periodic O&M Treatment: | ON: (Periodic O&M Repeats over measure life) |  |  |  | Elec Savings Shape Input Worksheet | GLSShapes | [8 empty] | Real After-Tax Cost of Capital | 0.04409 | 0.0223 | 0.0428 | 0.048 |  | Present Value Time Zero | 2022 |  | Bulk System T&D Credit ($/kw-yr)($/dailytherm-yr) | 3.08 | 0
| Limit Program Life to Measure Life: | ON: (Program life limited to measure life) |  |  |  | Marginal Gas Avoided Cost Input Worksheet | 2021P Gas | [8 empty] | Financial Life (years) | 12 | 1 | 1 | 1 |  | Input Cost Reference Year | 2016 |  | Bulk System T&D Credit - Applicable Peak Period (1,2, or both) | Peak Periods 1 and 2 | Peak Period 1 only
[6 empty] | Gas Savings Shape Input Worksheet | GLSShapes | [9 empty] | Customer | Wholesale Elec | Retail Elec | Nat Gas |  | Real Discount Rate | 0.0375 |  | Bulk System T&D I2R Loss Component (%) | 0.9 | N/A
[6 empty] | Marginal Elec CO2 per kWh Input Worksheet | CO2 lbs per kWh | [8 empty] | Sponsor Share of Initial Capital Cost | 0 | 0.3 | 0.7 | 0 |  | Capital Real Escalation Rate | 0 |  | Local System Dist Loss Factor | 0.047399 | 0
[6 empty] | Marginal Gas CO2 per therm Input Worksheet | CO2 lbs per therm | [8 empty] | Sponsor Share of Annual O&M | 0 | 0.3 | 0.7 | 0 |  | Admin Cost (as % of Initial Capital Cost) | 0.2 |  | Local System Dist Credit ($/kw-yr)($/dailytherm-yr) | 6.85 | 0
[6 empty] | Marginal Avoided Cost CO2 Input Worksheet | Dollars per ton CO2 | [8 empty] | Sponsor Share of Periodic Replacement Cost | 0 | 0.3 | 0.7 | 0 |  | Regional Act Conservation Credit (%) | 0 |  | Local System Dist Credit - Applicable Peak Period (1,2, or both) | Peak Periods 1 and 2 | Peak Period 1 only
[6 empty] | Peak Hours Definitions Input Worksheet | UtilityPeakHours | [8 empty] | Sponsor Share of Admin Cost |  | 0.3 | 0.7 | 0 |  | Report Annual Carbon Saved for Year | 2022 |  | Local System Dist I2R Loss Component (%) | 0.7 | N/A
[16 empty] | Last Year of Non-Customer O&M & Period Replacement |  | 20 | [6 empty] | Risk-Mitigation Credit (mills/kWh)(mills/therm) - Retro. | 0 | 0
[25 empty] | Risk-Mitigation Credit (mills/kWh)(mills/therm) - Lost Op. | 0 | 0
[25 empty] | Deferred Generation Capacity Credit - Same or Different Resources? | None - No Credit | N/A
[25 empty] | Deferred Generation Capacity Credit ($/bulk kW-year) - Peak 1 | 0 | N/A
[25 empty] | Deferred Generation Capacity Credit ($/bulk kW-year) - Peak 2 | 0 | N/A
Savings Component Results; Sorted in same order as input
Total Results |  | Measure Input Data | [11 empty] | Savings | [19 empty] | PV Capital |  |  |  | PV Admin |  |  |  | PV O&M |  |  |  | PV Periodic Repl. |  |  |  | Total PV Capital, O&M and Periodic Repl Costs |  |  |  |  | PV Wholesale Electric Utility Costs & Benefits | [6 empty] | PV Retail Electric Utility Costs & Benefits | [6 empty] | PV Electric Utility System Costs & Benefits | [5 empty] | Electric Utility System Economics |  | Sponsor Levelized Cost (mills/kwh) |  |  |  |  | PV Regional Costs & Benefits | [16 empty] | TRC Economics |  | Physical CO2 | [5 empty] | Gas Inputs |  |  |  | PV Gas Utility System Costs & Benefits |  |  |  |  | Gas Utility System Economics |  | Lifetime kWh denominators
Measure Application | Savings Component | Time Varying Savings? (Yes/No) | Measure Life (yrs) | Length of Period 1 (yrs) | Site Savings - Period 1 (kWh) | Site Savings - Period 2 (kWh) | Site Savings - Period 1 (therms) | Site Savings - Period 2 (therms) | Capital Cost ($) | PV Base Case Cost at Start of Period 2($) | Annual O&M Cost ($/unit) | PV Per. Repl. Cost ($/unit) | Load Shape (electric) | Wholesale Electric Energy - Period 1 (kWh) | Wholesale Electric Energy - Period 2 (kWh) | Wholesale Electric Demand - Period 1, Peak 1 (kW) | Wholesale Electric Demand - Period 1, Peak 2 (kW) | Wholesale Electric Demand - Period 2, Peak 1 (kW) | Wholesale Electric Demand - Period 2, Peak 2 (kW) | Retail Electric Demand - Period 1, Peak 1 (kW) | Retail Electric Demand - Period 1, Peak 2 (kW) | Retail Electric Demand - Period 2, Peak 1 (kW) | Retail Electric Demand - Period 2, Peak 2 (kW) | Wholesale Gas Energy - Period 1 (therms/yr) | Wholesale Gas Energy - Period 2 (therms/yr) | Wholesale Gas Demand - Period 1, Peak 1 (therms/day) | Wholesale Gas Demand - Period 1, Peak 2 (therms/day) | Wholesale Gas Demand - Period 2, Peak 1 (therms/day) | Wholesale Gas Demand - Period 2, Peak 2 (therms/day) | Retail Gas Demand - Period 1, Peak 1 (therms/day) | Retail Gas Demand - Period 1, Peak 2 (therms/day) | Retail Gas Demand - Period 2, Peak 1 (therms/day) | Retail Gas Demand - Period 2, Peak 2 (therms/day) | Wholesale Electric | Retail Electric | Natural Gas | Customer | Wholesale Electric | Retail Electric | Natural Gas | Customer | Wholesale Electric | Retail Electric | Natural Gas | Customer | Wholesale Electric | Retail Electric | Natural Gas | Customer | Wholesale Electric | Retail Electric | Natural Gas | Customer | Total | Wholesale Utility System Energy | Wholesale Utility System T&D Def. Cap. | Wholesale Utility System Act C-E Credit | Wholesale Utility System Risk Mitigation Benefit | Wholesale Utility System Total System Benefit | Wholesale Utility System Total Non-Consumer Cost | Wholesale Utility System B/C Ratio | Retail Utility System Energy | Retail Utility System T&D Def. Cap. | Retail Utility System Act C-E Credit | Retail Utility System Risk Mitigation Benefit | Retail Utility System Total System Benefit | Retail Utility System Total Non-Consumer Cost | Retail Utility System System B/C Ratio | Utility System Energy | Utility System T&D Def. Cap. | Utility System Act C-E Credit | Utility System Total Risk Mitigation Benefit | Utility System Total System Benefit | Utility System Total Non-Consumer Cost | Utility System Net Levelized Cost (Net of Elec T&D Capacity Benefits, Act Credit & Risk-Mitigation Benefit) in mills/kwh | Utility System System B/C Ratio | Wholesale Electric Levelized Cost | Retail Electric Levelized Cost | Natural Gas Levelized Cost | Customer Levelized Cost | Total Levelized Cost | PV Regional Electric Energy | PV Regional Gas Energy | PV Regional Electric T&D Def. Cap. | PV Regional Gas T&D Def. Cap. | PV Regional Electric Deferred Generation Capacity Credit, Peak 1 | PV Regional Electric Deferred Generation Capacity Credit, Peak 2 | PV Regional Electric and Gas Systems CO2 | PV Regional Electric System Risk-Mitigation Benefit | PV Regional Gas System Risk-Mitigation Benefit | PV Regional Non-E Value | PV Regional Act Credit | PV Regional Capital Cost | PV Regional Admin Cost | PV Regional Annual O&M Cost | PV Regional Periodic Replacement Cost | PV Total Regional Benefit | PV Total Regional Cost | TRC B/C Ratio | TRC Net Levelized Cost (Net of All Benefits) in mills/kWh | Electric System CO2 Avoided (Lifetime Tons) | Gas System CO2 Avoided (Lifetime Tons) | Total System CO2 Avoided (Lifetime Tons) | Electric System CO2 Avoided (Annual Tons in 2022) | Gas System CO2 Avoided (Annual Tons in 2022) | Total System CO2 Avoided (Annual Tons in 2022) | Gas Site Savings (therms) | Load Shape (gas) | Diversitfied Load Factor (gas) | Wholesale Coincidence Factor (gas) | Total Gas Utility System Energy | Gas Utility System T&D Def. Cap. | Gas Utility System Risk Mitigation Benefit | Gas Utility System Total System Benefit | Gas Utility System Total Non-Consumer Cost | Gas Utility System Net Levelized Cost (Net of Gas T&D Capacity Benefits & Risk-Mitigation Benefits) in cents/therm | Gas Utility System System B/C Ratio | PV Electricity Savings (kWh) (denominator for Levelized Cost) | Denominator for PV fields in MeasureTable
EMC-1 LDC with no VVO | 1 - LDC with no VVO | No | 15 |  | 1.5398 |  | 0 |  | 0.22989 |  | 0.017786 | 0 | S-All-UD-CVR-All-All-N | 1.7102 |  | 0.00023795 | 0.00022522 |  |  | 0.0002258 | 0.00021502 |  |  | 0 |  | n/a | n/a |  |  | n/a | n/a |  |  | 0.067958 | 0.16175 | 0 | 0 | (na) | (na) | (na) | (na) | 0.060375 | 0.14087 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12833 | 0.30262 | 0 | 0 | 0.43095 | 0.59855 | 0.0082928 | 0 | 0 | 0.60684 | 0.12833 | 4.7287 | 0.59855 | 0.017502 | 0 | 0 | 0.61605 | 0.30262 | 2.0357 | 0.59855 | 0.025794 | 0 | 0 | 0.62434 | 0.43095 | 20.9375 | 1.4487 | 6.6318 | 15.6386 | 0 | 0 | 22.2705 | 0.59855 | 0 | 0.025794 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22971 |  | 0.20125 | 0 | 0.62434 | 0.43095 | 1.4487 | 20.9375 | 0.011928 | 0 | 0.011928 | 0.00079522 | 0 | 0.00079522 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 9999 | 9999 | 19.3509 | 19.3509
ECM-2 & ECM-3 LDC with VVO & AMI | 2 - LDC with VVO and EOL | No | 15 |  | 6.4047 |  | 0 |  | 3.2849 |  | 0.16424 | 0 | S-All-UD-CVR-All-All-N | 7.1133 |  | 0.00098973 | 0.00093681 |  |  | 0.00093919 | 0.00089434 |  |  | 0 |  | n/a | n/a |  |  | n/a | n/a |  |  | 0.97103 | 2.3112 | 0 | 0 | (na) | (na) | (na) | (na) | 0.55754 | 1.3009 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5286 | 3.6121 | 0 | 0 | 5.1407 | 2.4896 | 0.034493 | 0 | 0 | 2.5241 | 1.5286 | 1.6513 | 2.4896 | 0.072796 | 0 | 0 | 2.5624 | 3.6121 | 0.7094 | 2.4896 | 0.10729 | 0 | 0 | 2.5969 | 5.1407 | 62.535 | 0.50517 | 18.9911 | 44.8769 | 0 | 0 | 63.868 | 2.4896 | 0 | 0.10729 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2822 |  | 1.8585 | 0 | 2.5969 | 5.1407 | 0.50517 | 62.535 | 0.049615 | 0 | 0.049615 | 0.0033077 | 0 | 0.0033077 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 9999 | 9999 | 80.4887 | 80.4887
ECM-2 & ECM-3 LDC with VVO & AMI | 3 - LDC with VVO and Existing AMI | No | 15 |  | 1.8187 |  | 0 |  | 0.031803 |  | 0.0015901 | 0 | S-All-UD-CVR-All-All-N | 2.0199 |  | 0.00028105 | 0.00026602 |  |  | 0.00026669 | 0.00025396 |  |  | 0 |  | n/a | n/a |  |  | n/a | n/a |  |  | 0.009401 | 0.022376 | 0 | 0 | (na) | (na) | (na) | (na) | 0.0053978 | 0.012595 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014799 | 0.034971 | 0 | 0 | 0.049769 | 0.70696 | 0.0097948 | 0 | 0 | 0.71675 | 0.014799 | 48.433 | 0.70696 | 0.020671 | 0 | 0 | 0.72763 | 0.034971 | 20.8069 | 0.70696 | 0.030466 | 0 | 0 | 0.73742 | 0.049769 | 0.84456 | 14.8168 | 0.64749 | 1.53 | 0 | 0 | 2.1775 | 0.70696 | 0 | 0.030466 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.031777 |  | 0.017993 | 0 | 0.73742 | 0.049769 | 14.8168 | 0.84456 | 0.014089 | 0 | 0.014089 | 0.00093926 | 0 | 0.00093926 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 9999 | 9999 | 22.8558 | 22.8558
Measure Application Results
Total Results |  | Measure Input Data | [11 empty] | Savings | [19 empty] | PV Capital |  |  |  | PV Admin |  |  |  | PV O&M |  |  |  | PV Periodic Repl. |  |  |  | Total PV Capital, O&M and Periodic Repl Costs |  |  |  |  | PV Wholesale Electric Utility Costs & Benefits | [6 empty] | PV Retail Electric Utility Costs & Benefits | [6 empty] | PV Electric Utility System Costs & Benefits | [5 empty] | Electric Utility System Economics |  | Sponsor Levelized Cost (mills/kwh) |  |  |  |  | PV Regional Costs & Benefits | [16 empty] | TRC Economics |  | Physical CO2 | [5 empty] | Gas Inputs |  |  |  | PV Gas Utility System Costs & Benefits |  |  |  |  | Gas Utility System Economics |  | Lifetime kWh denominators
Measure Application | Savings Component | Time Varying Savings? (Yes/No) | Measure Life (yrs) | Length of Period 1 (yrs) | Site Savings - Period 1 (kWh) | Site Savings - Period 2 (kWh) | Site Savings - Period 1 (therms) | Site Savings - Period 2 (therms) | Capital Cost ($) | PV Base Case Cost at Start of Period 2($) | Annual O&M Cost ($/unit) | PV Per. Repl. Cost ($/unit) | Load Shape (electric) | Wholesale Electric Energy - Period 1 (kWh) | Wholesale Electric Energy - Period 2 (kWh) | Wholesale Electric Demand - Period 1, Peak 1 (kW) | Wholesale Electric Demand - Period 1, Peak 2 (kW) | Wholesale Electric Demand - Period 2, Peak 1 (kW) | Wholesale Electric Demand - Period 2, Peak 2 (kW) | Retail Electric Demand - Period 1, Peak 1 (kW) | Retail Electric Demand - Period 1, Peak 2 (kW) | Retail Electric Demand - Period 2, Peak 1 (kW) | Retail Electric Demand - Period 2, Peak 2 (kW) | Wholesale Gas Energy - Period 1 (therms/yr) | Wholesale Gas Energy - Period 2 (therms/yr) | Wholesale Gas Demand - Period 1, Peak 1 (therms/day) | Wholesale Gas Demand - Period 1, Peak 2 (therms/day) | Wholesale Gas Demand - Period 2, Peak 1 (therms/day) | Wholesale Gas Demand - Period 2, Peak 2 (therms/day) | Retail Gas Demand - Period 1, Peak 1 (therms/day) | Retail Gas Demand - Period 1, Peak 2 (therms/day) | Retail Gas Demand - Period 2, Peak 1 (therms/day) | Retail Gas Demand - Period 2, Peak 2 (therms/day) | Wholesale Electric | Retail Electric | Natural Gas | Customer | Wholesale Electric | Retail Electric | Natural Gas | Customer | Wholesale Electric | Retail Electric | Natural Gas | Customer | Wholesale Electric | Retail Electric | Natural Gas | Customer | Wholesale Electric | Retail Electric | Natural Gas | Customer | Total | Wholesale Utility System Energy | Wholesale Utility System T&D Def. Cap. | Wholesale Utility System Act C-E Credit | Wholesale Utility System Risk Mitigation Benefit | Wholesale Utility System Total System Benefit | Wholesale Utility System Total Non-Consumer Cost | Wholesale Utility System B/C Ratio | Retail Utility System Energy | Retail Utility System T&D Def. Cap. | Retail Utility System Act C-E Credit | Retail Utility System Risk Mitigation Benefit | Retail Utility System Total System Benefit | Retail Utility System Total Non-Consumer Cost | Retail Utility System System B/C Ratio | Utility System Energy | Utility System T&D Def. Cap. | Utility System Act C-E Credit | Utility System Total Risk Mitigation Benefit | Utility System Total System Benefit | Utility System Total Non-Consumer Cost | Utility System Net Levelized Cost (Net of Elec T&D Capacity Benefits, Act Credit & Risk-Mitigation Benefit) in mills/kwh | Utility System System B/C Ratio | Wholesale Electric Levelized Cost | Retail Electric Levelized Cost | Natural Gas Levelized Cost | Customer Levelized Cost | Total Levelized Cost | PV Regional Electric Energy | PV Regional Gas Energy | PV Regional Electric T&D Def. Cap. | PV Regional Gas T&D Def. Cap. | PV Regional Electric Deferred Generation Capacity Credit, Peak 1 | PV Regional Electric Deferred Generation Capacity Credit, Peak 2 | PV Regional Electric and Gas Systems CO2 | PV Regional Electric System Risk-Mitigation Benefit | PV Regional Gas System Risk-Mitigation Benefit | PV Regional Non-E Value | PV Regional Act Credit | PV Regional Capital Cost | PV Regional Admin Cost | PV Regional Annual O&M Cost | PV Regional Periodic Replacement Cost | PV Total Regional Benefit | PV Total Regional Cost | TRC B/C Ratio | TRC Net Levelized Cost (Net of All Benefits) in mills/kWh | Electric System CO2 Avoided (Lifetime Tons) | Gas System CO2 Avoided (Lifetime Tons) | Total System CO2 Avoided (Lifetime Tons) | Electric System CO2 Avoided (Annual Tons in 2022) | Gas System CO2 Avoided (Annual Tons in 2022) | Total System CO2 Avoided (Annual Tons in 2022) | Gas Site Savings (therms) | Load Shape (gas) | Diversitfied Load Factor (gas) | Wholesale Coincidence Factor (gas) | Total Gas Utility System Energy | Gas Utility System T&D Def. Cap. | Gas Utility System Risk Mitigation Benefit | Gas Utility System Total System Benefit | Gas Utility System Total Non-Consumer Cost | Gas Utility System Net Levelized Cost (Net of Gas T&D Capacity Benefits & Risk-Mitigation Benefits) in cents/therm | Gas Utility System System B/C Ratio | PV Electricity Savings (kWh) (denominator for Levelized Cost) | Denominator for PV fields in MeasureTable
ECM-2 & ECM-3 LDC with VVO & AMI |  | No | 15 |  | 8.2234 |  | 0 |  | 3.3167 |  | 0.16583 | 0 | loadshape may vary by savings component | 9.1332 |  | 0.0012708 | 0.0012028 |  |  | 0.0012059 | 0.0011483 |  |  | 0 |  | n/a | n/a |  |  | n/a | n/a |  |  | 0.98043 | 2.3335 | 0 | 0 | 0.199 | 0.46434 | 0 | 0 | 0.56294 | 1.3135 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7424 | 4.1114 | 0 | 0 | 5.8538 | 3.1966 | 0.044288 | 0 | 0 | 3.2409 | 1.7424 | 1.86 | 3.1966 | 0.093468 | 0 | 0 | 3.29 | 4.1114 | 0.80022 | 3.1966 | 0.13776 | 0 | 0 | 3.3343 | 5.8538 | 55.3102 | 0.5696 | 16.8598 | 39.7834 | 0 | 0 | 56.6431 | 3.1966 | 0 | 0.13776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.314 | 0.66334 | 1.8765 | 0 | 3.3343 | 5.8538 | 0.5696 | 55.3102 | 0.063704 | 0 | 0.063704 | 0.0042469 | 0 | 0.0042469 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 9999 | 9999 | 103.3445 | 103.3445
EMC-1 LDC with no VVO |  | No | 15 |  | 1.5398 |  | 0 |  | 0.22989 |  | 0.017786 | 0 | loadshape may vary by savings component | 1.7102 |  | 0.00023795 | 0.00022522 |  |  | 0.0002258 | 0.00021502 |  |  | 0 |  | n/a | n/a |  |  | n/a | n/a |  |  | 0.067958 | 0.16175 | 0 | 0 | 0.013794 | 0.032185 | 0 | 0 | 0.060375 | 0.14087 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14213 | 0.33481 | 0 | 0 | 0.47693 | 0.59855 | 0.0082928 | 0 | 0 | 0.60684 | 0.14213 | 4.2697 | 0.59855 | 0.017502 | 0 | 0 | 0.61605 | 0.33481 | 1.84 | 0.59855 | 0.025794 | 0 | 0 | 0.62434 | 0.47693 | 23.3135 | 1.3091 | 7.3447 | 17.3019 | 0 | 0 | 24.6465 | 0.59855 | 0 | 0.025794 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22971 | 0.045979 | 0.20125 | 0 | 0.62434 | 0.47693 | 1.3091 | 23.3135 | 0.011928 | 0 | 0.011928 | 0.00079522 | 0 | 0.00079522 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 9999 | 9999 | 19.3509 | 19.3509
Supply Curve Results; Measure Applications sorted by TRC Net Levelized Cost
Totals for Categories with Benefits Exceeding Costs. Levelized cost is TRC Net Levelized Cost (Net of Benefits) | [12 empty] | Savings Allocation by Cost Bin and Month for Segments 1 | [12 empty] | Savings Allocation by Cost Bin and Month for Segments 2
| Totals Basis | Busbar Electric Savings in kWh | First Cost | Admin Cost | First Year Program Cost | PV Cost | PV Benefits | Unit Program Cost: First Year Program Cost in $/average annual kW saved | Utility System Net Levelized Cost (Net of T&D Capacity Benefits, Act Credit & Risk-Mitigation) in mills/kWh | TRC Net Levelized Cost (Net of All Benefits) in mills/kWh | TRC B/C Ratio | Net Electric & Gas System CO2 Avoided (Lifetime Tons) | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
| Measures with B/C > 1.00 | 3.7301 | 0.2617 | 0 | 0.2617 | 0.48072 | 1.3618 | 614.5906 | 10.0568 | 10.0568 | 8.6878 | 0.026017 | 0.05931 | 0.055115 | 0.063131 | 0.035328 | 0.034996 | 0.03535 | 0.060204 | 0.062441 | 0.057715 | 0.053472 | 0.048283 | 0.061655 |  | 0.30341 | 0.27021 | 0.29445 | 0.21986 | 0.22786 | 0.21992 | 0.26689 | 0.26393 | 0.25628 | 0.24037 | 0.23921 | 0.30067
| Categories with B/C > 1.00 | 1.7102 | 0.22989 | 0.045979 | 0.27587 | 0.47693 | 0.62434 | 1413.1113 | 23.3135 | 23.3135 | 1.3091 | 0.011928 | 0.17241 | 0.16022 | 0.18352 | 0.1027 | 0.10173 | 0.10276 | 0.17501 | 0.18152 | 0.16778 | 0.15544 | 0.14036 | 0.17923 |  | 0.88203 | 0.78551 | 0.85598 | 0.63914 | 0.66238 | 0.63931 | 0.77584 | 0.76724 | 0.74501 | 0.69877 | 0.69539 | 0.87405
Supply Curve Results: By TRC Net Levelized Cost - Net of Benefits
| Block 1: <= 0 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 2: <= 10 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 3: 10-20 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 4: 20-30 mills/kWh | 1.7102 | 0.22989 | 0.045979 | 0.27587 | 0.47693 | 0.62434 | 1413.1113 | 23.3135 | 23.3135 | 1.3091 | 0.011928 | 0.027192 | 0.025269 | 0.028944 | 0.016197 | 0.016045 | 0.016207 | 0.027602 | 0.028628 | 0.026461 | 0.024516 | 0.022137 | 0.028267 |  | 0.13911 | 0.12389 | 0.135 | 0.1008 | 0.10447 | 0.10083 | 0.12236 | 0.12101 | 0.1175 | 0.11021 | 0.10967 | 0.13785
| Block 5: 30-40 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 6: 40-50 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 7: 50-60 mills/kWh | 9.1332 | 3.3167 | 0.66334 | 3.98 | 5.8538 | 3.3343 | 3817.397 | 55.3102 | 55.3102 | 0.5696 | 0.063704 | 0.14522 | 0.13495 | 0.15458 | 0.086502 | 0.085689 | 0.086555 | 0.14741 | 0.15289 | 0.14132 | 0.13093 | 0.11822 | 0.15096 |  | 0.74292 | 0.66162 | 0.72098 | 0.53834 | 0.55791 | 0.53848 | 0.65348 | 0.64623 | 0.62751 | 0.58856 | 0.58571 | 0.7362
| Block 8: 60-70 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 9: 70-80 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 10: 80-90 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 11: 90-100 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 12: 100-110 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 13: 110-120 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 14: 120-130 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 15: 130-140 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 16: 140-150 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 17: 150-160 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 18: 160-170 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 19: 170-180 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 20: 180-190 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 21: 190-200 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Block 22: > 200 mills/kWh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Shaped Savings Results; By Category and sorted by TRC BC ratio
[13 empty] | Savings Allocation by Cost Bin and Month for Segments 1 Mar: Savings Allocation by Category and Month for Segments 1 |  |  |  | Savings Allocation by Category and Month for Segments 2
Category | Measure | Busbar Savings | First Cost | Admin Cost | First Year Program Cost | PV Cost | PV Benefits | Unit Program Cost: First Year Program Cost in $/average annual kW saved | Utility System Net Levelized Cost (Net of T&D Capacity Benefits, Act Credit & Risk-Mitigation) in mills/kWh | TRC Net Levelized Cost (Net of All Benefits) in mills/kWh | TRC B/C Ratio | Net Electric & Gas System CO2 Avoided (Lifetime Tons) | Wholesale KW - Peak 1 | Wholesale KW - Peak 2 | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
EMC-1 LDC with no VVO |  | 1.7102 | 0.22989 | 0.045979 | 0.27587 | 0.47693 | 0.62434 | 1413.1113 | 23.3135 | 23.3135 | 1.3091 | 0.011928 | 0.00023795 | 0.00022522 | 0.027192 | 0.025269 | 0.028944 | 0.016197 | 0.016045 | 0.016207 | 0.027602 | 0.028628 | 0.026461 | 0.024516 | 0.022137 | 0.028267 |  | 0.13911 | 0.12389 | 0.135 | 0.1008 | 0.10447 | 0.10083 | 0.12236 | 0.12101 | 0.1175 | 0.11021 | 0.10967 | 0.13785
ECM-2 & ECM-3 LDC with VVO & AMI |  | 9.1332 | 3.3167 | 0.66334 | 3.98 | 5.8538 | 3.3343 | 3817.397 | 55.3102 | 55.3102 | 0.5696 | 0.063704 | 0.0012708 | 0.0012028 | 0.14522 | 0.13495 | 0.15458 | 0.086502 | 0.085689 | 0.086555 | 0.14741 | 0.15289 | 0.14132 | 0.13093 | 0.11822 | 0.15096 |  | 0.74292 | 0.66162 | 0.72098 | 0.53834 | 0.55791 | 0.53848 | 0.65348 | 0.64623 | 0.62751 | 0.58856 | 0.58571 | 0.7362
Measure Inputs: used to check if inputs have changed since ProCost was run
COLUMN HASN'T CHANGED? >>
TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | TRUE | Savings Allocation by Category and Month for Segments 1 Jan: TRUE; Savings Allocation by Category and Month for Segments 1 Feb: TRUE; Savings Allocation by Category and Month for Segments 1 Mar: TRUE; Savings Allocation by Category and Month for Segments 1 Apr: TRUE
Measure Application | Savings Component | Savings for Period 1 (kwh/yr) | Measure Life (yrs) | Capital Cost | Annual O&M | Shape Pointer | Non-E Val ($/yr) | Cost A ($) | Replacement Period A (yrs) | Cost B ($) | Replacement Period B (yrs) | Cost C ($) | Replacement Period C (yrs) | Savings (therms/yr) | Savings Allocation by Category and Month for Segments 1 Jan: Shape Pointer; Savings Allocation by Category and Month for Segments 1 Feb: Savings for Period 2 (kWh/yr); Savings Allocation by Category and Month for Segments 1 Mar: Length of Period 1 (yrs); Savings Allocation by Category and Month for Segments 1 Apr: Base Case Cost at Start of Period 2 ($); Savings Allocation by Category and Month for Segments 1 May: ↓ROW HASN'T CHANGED?
EMC-1 LDC with no VVO | 1 - LDC with no VVO | 1.5398 | 15 | 0.22989 | 0.017786 | S-All-UD-CVR-All-All-N | [8 empty] | Savings Allocation by Category and Month for Segments 1 May: 0
ECM-2 & ECM-3 LDC with VVO & AMI | 2 - LDC with VVO and EOL | 6.4047 | 15 | 3.2849 | 0.16424 | S-All-UD-CVR-All-All-N | [8 empty] | Savings Allocation by Category and Month for Segments 1 May: 0
ECM-2 & ECM-3 LDC with VVO & AMI | 3 - LDC with VVO and Existing AMI | 1.8187 | 15 | 0.031803 | 0.0015901 | S-All-UD-CVR-All-All-N | [8 empty] | Savings Allocation by Category and Month for Segments 1 May: 0
0
Note on A7: :ProCost Measure Application: "Specific measure applications may be defined by characteristics of the affected building, end use, system, equipment or location. For example, wall insulation may be applied to single-family residences, with basements, located in the climate zone west of the Cascade Mountains." (Guidelines, Roadmap, Section 1.3.1) Each measure application may have multiple savings components: for example, an appliance measure may have Appliance Energy and HVAC Interaction components. See this field on the sheet "LookupTable" for naming convention.
Note on B7: :ProCost Savings component. User-defined. Refer to Standard Information Workbook for any naming conventions. Multiple savings components may be associated with a single measure application.
Note on C7: :ProCost Annual electric savings for the measure in kWh at the site. May be positive, negative or zero. Savings are incremental to the baseline alternative. For measure applications modeled with a single savings period, savings should be stated in this field.
Note on D7: :ProCost Physical life of the measure in years. Must be >=1. This is the effective useful life of the measure.
Note on E7: :ProCost Initial cost to install the measure in dollars. Costs are incremental to the baseline alternative. Dollars must be denominated in the same year as 'Input Cost Reference Year' input on the ProData page.
Note on F7: :ProCost Annual operations and maintenance cost for the measure in dollars. Must be incremental cost over the baseline alternative. May be positive, negative or zero. Dollars must be denominated in the same year as 'Input Cost Reference Year' input on the ProData page. O&M costs are entered as positive values. Negative values represent O&M savings compared to the baseline alternative. For measure applications modeled with two savings periods, these are the average incremental O&M costs over the entire measure life (both savings periods). Example: Annualized maintenance cost for a heat pump heating system compared to a baseline electric resistance heating system.
Note on G7: :ProCost Name of the pointer to the shape of the savings. The shapes represent the daily and monthly shape of the saving. Shape of the savings is relative to the baseline alternative. A list of shape names can be found on sheet "ValidationLists", in Column A. The data for these shapes are in the MC_AND_Loadshape file. For measure applications modeled with two savings periods, the same shape is used for both savings periods.
Note on H7: :ProCost Annual value of any non-energy benefits of the measure, relative to the baseline alternative. Expressed in dollars per year and denominated in dollars of the 'Cost Reference Year'. Positive value represents dollar savings. Negative value represents dollar cost. Example: Water, detergent and sewer savings from efficient clothes washer. For measure applications modeled with two savings periods, these are the average incremental O&M costs over the entire measure life (both savings periods).
Note on I7: : Cost in dollars that is incurred for Replacement Period A. Positive value if cost. Negative value if savings. Dollars must be denominated in the same year as 'Input Cost Reference Year' input on the ProData page.
Note on J7: :ProCost Duration of Replacement Period A. The time at which Replacment Period A costs, or savings, occur.
Note on K7: : Cost in dollars that is incurred for Replacement Period B. Positive value if cost. Negative value if savings. Dollars must be denominated in the same year as 'Input Cost Reference Year' input on the ProData page.
Note on L7: :ProCost Duration of Replacement Period B. The time at which Replacment Period B costs, or savings, occur.
Note on M7: : Cost in dollars that is incurred for Replacement Period C. Positive value if cost. Negative value if savings. Dollars must be denominated in the same year as 'Input Cost Reference Year' input on the ProData page.
Note on N7: :ProCost Duration of Replacement Period C. The time at which Replacment Period C costs, or savings, occur.
Note on O7: : Annual gas savings, or increases, in therms. For measure applications modeled with two savings periods, these are the gas savings in Period 1. The ratio of gas savings in Savings Period 1 to Savings Period 2 is assumed to be equal to the ratio of electric savings in Savings Period 1 to Savings Period 2.
Note on P7: :ProCost Name of the pointer to the shape of the savings. The shapes represent the daily and monthly shape of the savings in four time segments for each month of the year. Shape of the savings is relative to the baseline alternative. These shapes are in the MC_AND_Loadshape file.
Note on Q7: :ProCost For measure applications modeled with two savings periods, this is the savings during the second period. Leave blank if measure application has only one savings period.
Note on R7: :ProCost For measure applications modeled with two savings periods, this is the duration of the first period. Leave blank if measure application has only one savings period.
Note on S7: :ProCost The cost incurred in the base case (i.e.,counterfactual) at the start of Period 2. This is treated as a benefit (or negative cost) in ProCost. For an RUL measure, the base case cost is typically the cost of the current practice equipment that would have been incurred at the end of its life if the equipment were not retrofitted. Dollars must be denominated in the same year as "Input Costs Reference Year" on the ProData page in ProCost, discounted to the start of Period 2. Leave blank if measure application has only one savings period.
Note on CD37: Direct and program administrative costs incurred by the utility system minus benefits that accrue to the utility system.There are separate Utility System Net Levelized Costs for the electric and the gas system. Utility system benefits include deferred transmission and distribution system capacity, risk-mitigation and Regional Act credit all of which are user-determined inputs.Utility System benefits do not include any non-energy benefits such as, other-fuel benefits, O&M benefits or periodic replacement benefits which generally accrue to the customer or to non-utility sponsors. Utility System Net Levelized Costs correspond to Utility System B/C ratio with regard to the costs and benefits included. Benefits are subtracted from costs, then levelized over the life of the measure The Risk-Mitigation credit is used to determine program cost-effectiveness and impacts both the Utility System B/C ratio and the Utility System Net Levelized Cost. If the Risk-Mitigation credit is non-zero, the Utility System Net Levelized Cost will be reduced by the Risk-Mitigation benefit. When using ProCost to build conservation supply curves, the user should set the Risk-Mitigation Credit to zero so the credit is not reflected in the supply curves.
Note on CD45: Direct and program administrative costs incurred by the utility system minus benefits that accrue to the utility system.There are separate Utility System Net Levelized Costs for the electric and the gas system. Utility system benefits include deferred transmission and distribution system capacity, risk-mitigation and Regional Act credit all of which are user-determined inputs.Utility System benefits do not include any non-energy benefits such as, other-fuel benefits, O&M benefits or periodic replacement benefits which generally accrue to the customer or to non-utility sponsors. Utility System Net Levelized Costs correspond to Utility System B/C ratio with regard to the costs and benefits included. Benefits are subtracted from costs, then levelized over the life of the measure The Risk-Mitigation credit is used to determine program cost-effectiveness and impacts both the Utility System B/C ratio and the Utility System Net Levelized Cost. If the Risk-Mitigation credit is non-zero, the Utility System Net Levelized Cost will be reduced by the Risk-Mitigation benefit. When using ProCost to build conservation supply curves, the user should set the Risk-Mitigation Credit to zero so the credit is not reflected in the supply curves.
Note on CJ37: Direct and program administrative costs of the measure to sponsor. Separate costs for each sponsor. Depends on share of costs incurred by sponsor, sponsor cost of capital, and financing term which are user-defined inputs. Includes applicable Capital, O&M, Periodic Replacement and Program Administrative costs. Sponsor costs are levelized over program life. Does not include any adjustments for benefit. NOTE: Units are per kWh for 'Electric' runs and per therm for 'Gas' runs for all sponsors.
Note on CJ45: Direct and program administrative costs of the measure to sponsor. Separate costs for each sponsor. Depends on share of costs incurred by sponsor, sponsor cost of capital, and financing term which are user-defined inputs. Includes applicable Capital, O&M, Periodic Replacement and Program Administrative costs. Sponsor costs are levelized over program life. Does not include any adjustments for benefit. NOTE: Units are per kWh for 'Electric' runs and per therm for 'Gas' runs for all sponsors.
Note on CW37: All costs minus all benefits regardless of which sponsor incurs the cost or accrues the benefits. TRC Net Levelized Cost includes all applicable costs and all benefits. In addition to energy system costs and benefits, TRC Net Levelized Cost includes non-energy, other-fuel, O&M, periodic-replacement and risk-mitigation benefits and costs. TRC Net Levelized Cost corresponds to TRC B/C ratios with regard to the costs and benefits included. Benefits are subtracted from costs, then levelized over the life of the measure. The Risk-Mitigation credit is used to determine program cost-effectiveness and impacts both the TRC B/C ratio and the TRC Net Levelized Cost. If Risk-Mitigation credit is non-zero, TRC Levelized Cost will be reduced by the risk-mitigation benefit. When using ProCost to build conservation supply curves, the user should set the Risk-Mitigation Credit to zero so the credit is not reflected in the supply curves.
Note on CW45: All costs minus all benefits regardless of which sponsor incurs the cost or accrues the benefits. TRC Net Levelized Cost includes all applicable costs and all benefits. In addition to energy system costs and benefits, TRC Net Levelized Cost includes non-energy, other-fuel, O&M, periodic-replacement and risk-mitigation benefits and costs. TRC Net Levelized Cost corresponds to TRC B/C ratios with regard to the costs and benefits included. Benefits are subtracted from costs, then levelized over the life of the measure. The Risk-Mitigation credit is used to determine program cost-effectiveness and impacts both the TRC B/C ratio and the TRC Net Levelized Cost. If Risk-Mitigation credit is non-zero, TRC Levelized Cost will be reduced by the risk-mitigation benefit. When using ProCost to build conservation supply curves, the user should set the Risk-Mitigation Credit to zero so the credit is not reflected in the supply curves.
Note on DO37: Direct and program administrative costs incurred by the utility system minus benefits that accrue to the utility system.There are separate Utility System Net Levelized Costs for the electric and the gas system. Utility system benefits include deferred transmission and distribution system capacity, risk-mitigation and Regional Act credit all of which are user-determined inputs.Utility System benefits do not include any non-energy benefits such as, other-fuel benefits, O&M benefits or periodic replacement benefits which generally accrue to the customer or to non-utility sponsors. Utility System Net Levelized Costs correspond to Utility System B/C ratio with regard to the costs and benefits included. Benefits are subtracted from costs, then levelized over the life of the measure The Risk-Mitigation credit is used to determine program cost-effectiveness and impacts both the Utility System B/C ratio and the Utility System Net Levelized Cost. If the Risk-Mitigation credit is non-zero, the Utility System Net Levelized Cost will be reduced by the Risk-Mitigation benefit. When using ProCost to build conservation supply curves, the user should set the Risk-Mitigation Credit to zero so the credit is not reflected in the supply curves.
Note on DO45: Direct and program administrative costs incurred by the utility system minus benefits that accrue to the utility system.There are separate Utility System Net Levelized Costs for the electric and the gas system. Utility system benefits include deferred transmission and distribution system capacity, risk-mitigation and Regional Act credit all of which are user-determined inputs.Utility System benefits do not include any non-energy benefits such as, other-fuel benefits, O&M benefits or periodic replacement benefits which generally accrue to the customer or to non-utility sponsors. Utility System Net Levelized Costs correspond to Utility System B/C ratio with regard to the costs and benefits included. Benefits are subtracted from costs, then levelized over the life of the measure The Risk-Mitigation credit is used to determine program cost-effectiveness and impacts both the Utility System B/C ratio and the Utility System Net Levelized Cost. If the Risk-Mitigation credit is non-zero, the Utility System Net Levelized Cost will be reduced by the Risk-Mitigation benefit. When using ProCost to build conservation supply curves, the user should set the Risk-Mitigation Credit to zero so the credit is not reflected in the supply curves.

## Roll Up
Flag: Analysis for Region, or only BPA Family? (Default = Region) | Region
Potential and Costs by Measure
Measures are all incremental. For Capital Costs, this is done directly in the costs on the Input Data sheet which carry through to the System Analysis sheet. No further work needed here. The savings in the System Analysis sheet are total, not incremental, so here we need to do subtraction. Measure 2 savings are made incremental by taking total ECM2 savings and subtracting ECM1 (ECM2,incremental = ECM2 - ECM1). Likewise, Measure 3 savings are made incremental by subtracting the incremental savings from ECM2 and the initial savings of ECM1 (ECM3,incremental = ECM3 - ECM2,incremental - ECM1) The gross potential is the potential potential based on 2018 Sales Since DEI/CVR scales with Sales, the gross potential is converted to a savings per unit (in this case, MWh, but for other measures it could be houses, etc.) and is later multiplied by the sales forecast in SC-Retro to estimate the going forward savings potential as sales change
| Gross Potential |  |  | Potential per MWh of 2018 Sales
| Savings Potential (MWh) | Capital Cost ($) | O&M Cost ($/yr) | Savings Potential (kWh Saved/kWh of Sales) | Capital Cost ($/MWh of Sales) | O&M Cost ($/yr/MWh of Sales) | Measure Life
Measure 1: LDC with no VVO | 264358.6477 | 39469099.6344 | 3053500 | 1.5398 | 0.22989 | 0.017786 | 15
Measure 2: LDC with VVO and EOL | 1099578.8994 | 563961000 | 28198050 | 6.4047 | 3.2849 | 0.16424 | 15
Measure 3: LDC with VVO and Existing AMI | 312239.5109 | 5460000 | 273000 | 1.8187 | 0.031803 | 0.0015901 | 15
FYI: The 7th Plan Methodology estimated ~2M MWh at a total cost of 720$M for a total $/Kwh of | 0.36 | And incl. O&M of 3.5$M | 0.36175
With the current numbers, this methodology is suggesting ~1.61M MWh savings at a cost of $654M for a total $/KWh of | 0.36326 | And incl. O&M of 31$M | 0.38207
Note on A2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Council staff uses the BPA Family selection only for scenario analysis specifically around BPA's customers. Practically, this is all utilities except the six IOUs, and the three mid- C utilities; Grant, Chelan, Douglas.

## Input Data
Percentage of Load Per Customer Class Applicable for Energy Savings
The residential and commercial numbers are adopted from Page 4-4 of RW Beck Study: "Table 4-1, Percent of Energy by Customer Class, shows the percent of energy by customer type that was included in determining the potential energy savings for each utility. Percent of Energy by Customer Class increased as more system improvements were accounted for in the options.", recognizing that the RW Beck study defined ECMs in a different way than is defined here in this workbook. Additionally, in the 6th and 7th Plans, industrial load was set to 0% eligible for all ECMs. The 2021 Plan revised this assumption and and made a portion of industrial load eligible for the following reasons: 1) Utility operations which lower system voltage will flow through to any "light" industrial customers, i.e. those without voltage controlling equipment on site 2) Staff at BPA used one-line transformer data to roughly estimate the amount of industrial load which would really need to be addressed at a facility level vs. lowering distribution head voltages. On the basis of that analysis, the eligible industrial load below is assumed to be very, very conservative as substantial additional industrial savings may be realizable with distrubution work even absent facility level upgrades. Future work could develop an additional ECM focused on collaborating with large industrial customers for facility upgrades and, in the process, upwardly revise the eligible fraction in ECM1/2/3 as consesus around the sensitivity of industrial loads to system voltage is built.
% of load eligible
Customer Class | ECM1 | ECM2 | ECM3
Residential | 70% | 80% | 85%
Commercial | 40% | 50% | 60%
Industrial/Other | 5% | 10% | 15%
dV and CVRf Data
Baseline Set-Point: The assumed target voltage at the substation. Based on lit review. Only used when utility specific data is not known. Initial Basis Voltage Change: How far you can push voltage down and feel confident that you will be within ANSI standards based on available telemetry (where ECM1 adds no telemetry, ECM2 adds EOL, and ECM3 directly monitors secondary voltage through AMI). Data developed in collaboration with BPA. Initial CVRf: Energy saved relative to voltage change. Voltage dependent, with a better CVRf at higher voltages, and declining either as your initial set point voltage is lower, or as you push voltage down deeper with CVR. A plot of secondary voltage (y-axis) vs. CVRf (x-axis) would look roughly parabolic. The initial CVRf numbers chosen here are estimated in collaboration with BPA (& are supported by the RW Beck study) and were selected to reflect the parabolic shape. CVRf Effectiveness Modifier: Estimation of relative effectiveness of CVRf based on HVAC composition driven by heating and cooling zone. Electric resistance heating save very little energy with CVR and since this spreadsheet is based on sales, we need to reduce the effectiveness of CVR (via the CVRf) in areas where that type of heating may significantly contribute to sales. On the other hand, inductive HVAC (heat pumps, AC) actually tends to have higher than normal CVR factors despite being thermostatically controlled. The ultimate formula is (Base CVRf)*(HZ Effectiveness Modifier)*(CZ Effectiveness Modifier). - Note: Effectiveness numbers are estimated based on a lit review + data in the 2007 RW Beck Study showing CVR factor by utility, HVAC type, and season in combination with Heating Cooling Zone Data from the RTF.
| ECM1 | ECM2 | ECM3
Assumed Baseline Set-Point (V) | 123
| ECM1 | ECM2 | ECM3
Initial Basis Voltage Change (V) | 1.2 | 3.6 | 5.4
Initial CVRf (pu) | 0.7 | 0.65 | 0.5
| Heating Zone 1 | Heating Zone 2 | Heating Zone 3
CVRf Effectiveness Modifier - Heating Zone (%) | 95% | 90% | 80%
| Cooling Zone 1 | Cooling Zone 2 | Cooling Zone 3
CVRf Effectiveness Modifier - Cooling Zone (%) | 85% | 90% | 100%
Cost Estimation
Click in this cell to see the full details Council staff worked closely with experts at BPA and took their comment to help develop a detailed, bottoms up costing of the equipment needed to enable each measure. This breakdown is: ECM1 “CVR with no VO (voltage optimization)”: Apply LDC to extant VR controls, substation only Assumptions: - Substation VR means in place - VR device(s) fitted with settable controls - Instrumentation and required signal sources in place - No new equipment, no changes to extant (or absent) instrument communications New Spend: Cost limited to engineering and instrument technician activity: [engr] $10k estimate R/X parameters for LDC, per feeder [engr] $5k optimal settings for aggregated feeder control (LTC) [tech] $5k apply and test settings in VR controls, per device (Assume urban = 0 per feeder, rural = 1 per feeder) ECM2 “CVR with Primary VO”: Apply SCADA Telemetry to all remote Primary assets, deploy asset coordinating VO algorithm at Dispatch Assumptions: - Extant substation instrumentation per ECM1 assumed - Remote (outside substation) VR devices fitted with controls - Remote switched capacitors fitted with controls, includes neutral CT - Remote voltage metering node (EoL) required, one per feeder - SCADA communications infrastructure deployed to substations only New Spend: Cost element – SCADA telemetry to remote primary assets [engr] $200k RF system design, typical terrain and reach [eqpt] $100k RF base equipment/structure deploy [eqpt] $100k RF repeat node, assume 2 @ $50k [eqpt] $5k/ea RF equipment per terminal node (remote asset) [tech] $100k deploy system parameters, test, commission Cost element – EoL node (One per feeder, priced per each) [eqpt] $10k 3x PTs, cutouts, enclosed (at least NEMA 4) instrumentation [engr] $2k device configuration (RF part covered above) [tech] $10k field deploy, hot work Cost element – new switched capacitor node (Assume 1 per urban feeder and 1 per rural feeder, priced per each) [eqpt] $25k capacitor, switch, 1x CT, 1x PT, enclosed control [engr] $2k device configuration [tech] $10k field deploy, hot work Cost element – coordinated VO algorithm [eqpt] $50k Could be offset through a program with BPA in the future for Publics [engr] $150k configure/commission engineering for each utility (medium size org) ECM3 “CVR with Primary VO & Secondary Monitoring”: Secondary distribution performance estimation using AMI signals, coordinated VO settings Assumptions: - Extant primary SCADA infrastructure per ECM2 assumed - Extant AMI system completely deployed assumed New Spend: - Cost element – SCADA access to MDM signal data [eqpt] $10k misc network appliances, possibly a proxy host (this is a WAG) [engr] $100k mutual systems (MDM <> SCADA) configuration for data exchange [eqpt] $50k Could be offset through a program with BPA in the future for Publics [engr] $50k algorithm configure/commission engineering for each utility Summary demonstrating how ECM2 costs were grouped as below: Per System: 700k from these elements: Cost element – SCADA telemetry to remote primary assets [engr] $200k RF system design, typical terrain and reach [eqpt] $100k RF base equipment/structure deploy [eqpt] $100k RF repeat node, assume 2 @ $50k [tech] $100k deploy system parameters, test, commission Cost element – coordinated VO algorithm [eqpt] $50k Could be offset through a program with BPA in the future for Publics [engr] $150k configure/commission engineering for each utility (medium size org) Per Sub: N/A Per Urban Feeder: Assuming 1x new EOL Node, 2x new switched caps, and RF for the three new pieces New EOL: 22k New Caps: 37k/ea = 72k RF: 5k/node = 15k All together: 109k/rural feeder Per Rural Feeder: Assuming 1x existing midline VR, 1x new EOL Node, 2x new switched caps, and RF for the existing mid-line VR + three new pieces New EOL: 22k New Caps: 37k/ea = 72k RF: 5k/node = 20k All together: 114k/rural feeder On the O&M side, this methodology uses 5% currently and could be improved in the future with better estimates of typical O&M costs for devices not associated with VO/CVR. With these numbers, the following guidance from BPA could be applied: 1 - for new primary instrumentation assets: - apply cost metric consistent with utility’s prior practice for instrumentation, which varies depending on presence of on-line diagnostics reported via SCADA and on engineering management approach (eg settings review); - apply R&R cost metric based on history of failures (defects, accidents, fault transients, weather events for field sited devices) of similar instruments; - note that there is no cost element specifically traceable to VO operations, except of course the existence of the instrument. 2 - for new primary element assets (VRs and switched Caps), the O&M costs are identical to those of extant assets, except as noted in 4. 3 - assuming that telemetry to field sited instruments is deployed specifically for supporting VO operations, AND that proper engineering practices for RF site design/construction were followed, high quality RF equipment will survive the environment for at least 15 years, except for instances of some severe weather events, which can be estimated statistically. 4 - for both extant and new primary elements, the O&M costs under proper VO operation are less than the historical non-VO costs, since proper VO has been shown to reduce both thermal and operational (mechanical) stresses on these assets. One can safely assume that VO operations will result in a reduction of VR tap change events by about 20% and a reduction of capacitor switching events by about 50%. BUT … The extension of the MTBF for these assets is much greater than these rate reductions might suggest, since the equipment lifetimes are not linearly related to these rates, instead being roughly characterized by suitable Weibull densities. 5 - the biggest headache is likely to be maintenance of the VO algorithm host platform, mainly the host OS security, SCADA software, and communication assets (RTUs being the salient problem here). I would note that these costs are subject to accounting considerations if the utility operates SCADA as a matter of routine.
|  | Per Utility | Per Customer ($2016) | Per Substation ($2016) | Per Urban/Suburban Feeder ($2016) | Per Rural Feeder ($2016) | Select Cost Inputs
ECM1 | CapEx | 0 | 0 | 5000 | 10000 | 15000
| O&M | 0 | 0 | 250 | 500 | 750 | ECM O&M Cost Adder | 5%
ECM2 | CapEx | 700000 | 0 | 0 | 109000 | 114000
| O&M | 35000 | 0 | 0 | 5450 | 5700
ECM3 | CapEx | 210000 | 0 | 0 | 0 | 0
| O&M | 10500 | 0 | 0 | 0 | 0
Substation & Feeder Estimation
Used to estimate the number of substations at a utility where the actual data cannot be found. The approach of bucketing by customers (rather than sales) is based on a calibration done in collaboration with BPA to check this methodology for substation estimation against some actual data for a larger set of utilities than is publically available. On the basis of this calibration and a check against actuals (which are not shared here due to them not having been made available by the publics directly), this methodology is confirmed to be sufficiently accurate for planning work. Across the entire system, this estimation methodology landed within 2% of the total number of distribution substations, with the estimates for individual utilities of course being a bit higher or a bit lower than actuals. For reference, on the whole, the methodology used in the 7th Plan produced an substation estimate that was ~40% lower than the actual system total based on the analysis done for this work. Feeder counts could not be checked against actuals due to a lack of available information (BPA only has insight of regional utilitiy dx down to the transformer level). Future work could invite more public utilities to share information about their system, especially given that IOUs already publish substation count (FERC Form 1) and feeder information (Reliability Reports filed with PUCs).
| Total Number of Customers | Customers per Substation | Feeders per Sub Estimate | % Of Feeders that are Urban/Suburban | % Of Feeders that are Rural
Bottom | 0 | 0 | 0 | 0% | 0%
Very Small Utility | 10000 | 1400 | 1.5 | 30% | 70%
Small Utility | 25000 | 1800 | 1.7 | 50% | 50%
Medium Utility | 50000 | 2500 | 2.2 | 65% | 35%
Large Utility | N/A | 5000 | 2.8 | 70% | 30%

## System Analysis
[19 empty] | ECM1: LDC without Voltage/Var Optimization (VVO, or simply VO) Lowers the distribution voltage level only using LDC without any system improvements for voltage optimization. |  |  |  |  | ECM2: LDC with Voltage Optimization Includes Option 1 and adds system improvements including var management and end of line metering. |  |  |  |  | ECM3: LDC with Voltage Optimization and Existing EMI Includes Option 2 ands secondary voltage monitoring through existing AMI ** Note: The ECM3 savings for utilities without AMI is simply a copy and paste of the savings from ECM2 at no additional incremental cost. It is important to carry over the ECM2 savings instead of setting it to zero because in the roll up tab, the savings from ECM1 are subtracted ECM2, and likewise the savings from ECM2 are subtracted from ECM3. For a utility without AMI, setting the savings in ECM3 to zero would result in a negative savings in the roll up since (0 [ECM3] - any number [ECM2] = negative). So, while a bit confusing, it is mathematically necessary to carry over ECM2 MWh savings to ECM3 for any utility without existing AMI. This is not done for costs because costs are already incremental in these sheets.***
[19 empty] | ECM1 |  |  |  |  | ECM2 |  |  |  |  | ECM3
Utility Name | null 1 | Exclude if Power Marketer or Behind the Meter | Existing AMI? | BPA Family? | Heating Zone | Cooling Zone | Total Number of Customers 2018 (n) | Annual Energy 2018 (MWh) | Residential Sales 2018 (MWh) | Commercial Sales 2018 (MWh) | Industrial/Other Sales 2018 (MWh) | Res & Comm Total Sales 2018 (MWh) | Res & Comm Share of Sales 2018 (%) | null2 | Total Distribution Subs 2018 (#) | Res/Comm Distribution Subs 2018 (#) | Total Urban Feeders 2018 (#) | Total Rural Feeders 2018 (#) | Base % dV | CVRf | Savings (MWh) | Capital Cost ($) | O&M Cost ($) | Base % dV | Base CVRf | Savings (MWh) | Cost (Incremental to ECM1) ($) | O&M Cost (Incremental to ECM1) ($) | Base % dV | Base CVRf | Savings (MWh) | Cost (Incremental to ECM2) ($) | O&M Cost (Incremental to ECM2) ($)
Puget Sound Energy Inc |  | 0 | Yes | No | 1 | 1 | 1149781 | 22725923 | 10497389 | 9038758 | 3189776 | 19536147 | 85.96% |  | 349 | 300.0149 | 588 | 252 | 0.9756% | 0.56525 | 61340.1817 | 11160074.4531 | 570250 | 2.927% | 0.52487 | 203338.1286 | 93520000 | 4676000 | 4.39% | 0.40375 | 262773.3346 | 210000 | 10500
PacifiCorp |  | 0 | Yes | No | 1 | 2 | 798332 | 20852804 | 7779810 | 7695254 | 5377740 | 15475064 | 74.21% |  | 291 | 215.9539 | 423 | 181 | 0.9756% | 0.5985 | 0 | 0 | 420000 | 2.927% | 0.55575 | 172568.4917 | 67441000 | 3372050 | 4.39% | 0.4275 | 225907.4058 | 210000 | 10500
Portland General Electric Company |  | 0 | Yes | No | 1 | 2 | 888123 | 19221496 | 7415759 | 7375419 | 4430318 | 14791178 | 76.95% |  | 164 | 126.2 | 247 | 106 | 0.9756% | 0.5985 | 0 | 0 | 244000 | 2.927% | 0.55575 | 163688.954 | 39707000 | 1985350 | 4.39% | 0.4275 | 213830.8043 | 210000 | 10500
Idaho Power Co |  | 0 | Yes | No | 1 | 3 | 551455 | 14586522 | 5134576 | 4104941 | 5347005 | 9239517 | 63.34% |  | 214 | 135.5537 | 266 | 114 | 0.9756% | 0.665 | 35705.8278 | 5047768.3666 | 272000 | 2.927% | 0.6175 | 120996.8381 | 42690000 | 2134500 | 4.39% | 0.475 | 159101.0057 | 210000 | 10500
Seattle City of |  | 0 | Yes | Yes | 1 | 1 | 461523 | 9074061 | 3000403 | 5021154 | 1052504 | 8021557 | 88.4% |  | 93 | 82.2129 | 161 | 69 | 0.9756% | 0.56525 | 22948.427 | 3056064.4622 | 155500 | 2.927% | 0.52487 | 77059.072 | 26115000 | 1305750 | 4.39% | 0.40375 | 101406.6279 | 210000 | 10500
Avista Corp |  | 0 | Yes | No | 2 | 2 | 387662 | 8587540 | 3626871 | 3188388 | 1772281 | 6815259 | 79.36% |  | 130 | 103.1708 | 185 | 104 | 0.9756% | 0.567 | 0 | 0 | 203000 | 2.927% | 0.5265 | 72008.5405 | 32721000 | 1636050 | 4.39% | 0.405 | 93555.8647 | 210000 | 10500
Snohomish County PUD No 1 |  | 0 | No | Yes | 1 | 1 | 350467 | 6481740 | 3566730 | 2386767 | 528243 | 5953497 | 91.85% |  | 71 | 65.2137 | 128 | 55 | 0.9756% | 0.56525 | 0 | 0 | 123000 | 2.927% | 0.52487 | 62978.7292 | 20922000 | 1046100 | 4.39% | 0.40375 | 62978.7292 | 0 | 0
Bonneville Power Administration |  | 0 | No | Yes | 1 | 2 | 10 | 2506132 | 0 | 782505 | 1723627 | 782505 | 31.22% |  | 21 | 6.557 | 3 | 44 | 0.9756% | 0.5985 | 2330.8413 | 722784.7955 | 39750 | 2.927% | 0.55575 | 9167.6824 | 6043000 | 302150 | 4.39% | 0.4275 | 9167.6824 | 0 | 0
Industrial Load No Longer Served by BPA |  |  | No | No | 1 | 1 | 1 | 3400000 | 0 | 0 | 3400000 | 0 | 0% |  | 1 | 0 | 0 | 1 | 0.9756% | 0.56525 | 937.4878 | 15000 | 500 | 2.927% | 0.52487 | 5223.1463 | 814000 | 40700 | 4.39% | 0.40375 | 5223.1463 | 0 | 0 | 0
PUD No 2 of Grant County |  | 0 | Yes | No | 1 | 3 | 50688 | 4910755 | 765978 | 961590 | 3183187 | 1727568 | 35.18% |  | 11 | 3.8697 | 8 | 3 | 0.9756% | 0.665 | 7006.6992 | 144348.6012 | 9000 | 2.927% | 0.6175 | 25517.4393 | 1914000 | 95700 | 4.39% | 0.475 | 35566.193 | 210000 | 10500
PUD No 1 of Cowlitz County |  | 0 | Yes | Yes | 1 | 1 | 50751 | 4839889 | 711762 | 382495 | 3745632 | 1094257 | 22.61% |  | 11 | 2.487 | 5 | 2 | 0.9756% | 0.56525 | 4624.0924 | 92435.0238 | 6750 | 2.927% | 0.52487 | 17439.4758 | 1473000 | 73650 | 4.39% | 0.40375 | 24750.9691 | 210000 | 10500
Tacoma City of |  | 0 | Yes | Yes | 1 | 1 | 177725 | 4617233 | 1863660 | 328887 | 2424686 | 2192547 | 47.49% |  | 36 | 17.095 | 34 | 14 | 0.9756% | 0.56525 | 8588.2216 | 635475.1016 | 36500 | 2.927% | 0.52487 | 29154.9899 | 6002000 | 300100 | 4.39% | 0.40375 | 38024.0226 | 210000 | 10500
PUD No 1 of Clark County |  | 0 | No | Yes | 1 | 2 | 208717 | 4465033 | 2364873 | 1335558 | 764602 | 3700431 | 82.88% |  | 42 | 34.8078 | 68 | 29 | 0.9756% | 0.5985 | 13008.5546 | 1289039.1415 | 66250 | 2.927% | 0.55575 | 42879.0284 | 11418000 | 570900 | 4.39% | 0.4275 | 42879.0284 | 0 | 0
NorthWestern Corporation |  | 0 | No | No | 3 | 3 | 112016.9457 | 3037016.4981 | 757200.4068 | 1277993.3124 | 1001822.7789 | 2035193.7192 | 67.01% |  | 23 | 15.413 | 30 | 13 | 0.9756% | 0.56 | 5962.3815 | 572064.8687 | 30500 | 2.927% | 0.52 | 20469.3195 | 5452000 | 272600 | 4.39% | 0.4 | 20469.3195 | 0 | 0
Umatilla Electric Coop Assn |  | 0 | Yes | Yes | 1 | 3 | 15288 | 2532517 | 166846 | 210511 | 2155160 | 377357 | 14.9% |  | 9 | 1.341 | 1 | 1 | 0.9756% | 0.665 | 2003.1396 | 31705.2126 | 3500 | 2.927% | 0.6175 | 8209.7071 | 923000 | 46150 | 4.39% | 0.475 | 12332.8474 | 210000 | 10500
City of Eugene |  | 0 | Yes | Yes | 1 | 2 | 93962 | 2341954 | 914487 | 869518 | 557949 | 1784005 | 76.18% |  | 19 | 14.4734 | 28 | 12 | 0.9756% | 0.5985 | 5931.5469 | 532367.1238 | 27750 | 2.927% | 0.55575 | 19879.2073 | 5120000 | 256000 | 4.39% | 0.4275 | 25951.2392 | 210000 | 10500
PUD No 1 of Benton County |  | 0 | Yes | Yes | 1 | 3 | 53744 | 1740849 | 698135 | 552107 | 490607 | 1250242 | 71.82% |  | 11 | 7.9 | 15 | 7 | 0.9756% | 0.665 | 4762.4877 | 294499.8705 | 15500 | 2.927% | 0.6175 | 15969.8549 | 3133000 | 156650 | 4.39% | 0.475 | 20817.5817 | 210000 | 10500
PUD No 1 of Chelan County |  | 0 | No | No | 1 | 3 | 50456 | 1635017 | 809774 | 486579 | 338664 | 1296353 | 79.29% |  | 11 | 8.7216 | 17 | 7 | 0.9756% | 0.665 | 5050.1501 | 318607.7515 | 16500 | 2.927% | 0.6175 | 16717.2329 | 3351000 | 167550 | 4.39% | 0.475 | 16717.2329 | 0 | 0
Flathead Electric Coop Inc |  | 0 | Yes | Yes | 3 | 3 | 66911 | 1452386 | 754053 | 457949 | 240384 | 1212002 | 83.45% |  | 14 | 11.6829 | 23 | 10 | 0.9756% | 0.56 | 3950.2449 | 438414.3196 | 22500 | 2.927% | 0.52 | 13031.788 | 4347000 | 217350 | 4.39% | 0.4 | 16714.0458 | 210000 | 10500
Central Lincoln People's Ut Dt |  | 0 | Yes | No | 1 | 1 | 39181 | 1296364 | 415852 | 191006 | 689506 | 606858 | 46.81% |  | 16 | 7.49 | 11 | 6 | 0.9756% | 0.56525 | 2216.7401 | 237449.852 | 14000 | 2.927% | 0.52487 | 7637.0879 | 2583000 | 129150 | 4.39% | 0.40375 | 10130.2516 | 210000 | 10500
PUD No 1 of Franklin County |  | 0 | No | Yes | 1 | 3 | 27180 | 1042834 | 357358 | 398435 | 287041 | 755793 | 72.47% |  | 11 | 7.9722 | 11 | 6 | 0.9756% | 0.665 | 2750.029 | 239861.2003 | 12750 | 2.927% | 0.6175 | 9286.1397 | 2583000 | 129150 | 4.39% | 0.475 | 9286.1397 | 0 | 0
Clatskanie Peoples Util Dist |  | 0 | No | Yes | 1 | 1 | 4201 | 1019901 | 72896 | 17193 | 929812 | 90089 | 8.833% |  | 4 | 0.35332 | 0 | 0 | 0.9756% | 0.56525 | 575.7002 | 1766.6224 | 1000 | 2.927% | 0.52487 | 2456.3305 | 700000 | 35000 | 4.39% | 0.40375 | 2456.3305 | 0 | 0
PUD No 1 of Douglas County |  | 0 | No | No | 1 | 3 | 15755 | 1005717 | 423075 | 381532 | 201110 | 804607 | 80% |  | 9 | 7.2003 | 6 | 6 | 0.9756% | 0.665 | 2976.7398 | 186001.4945 | 9750 | 2.927% | 0.6175 | 9928.2614 | 2038000 | 101900 | 4.39% | 0.475 | 9928.2614 | 0 | 0
PUD No 1 of Pend Oreille Cnty |  | 0 | No | Yes | 2 | 2 | 9310 | 999951 | 145245 | 52432 | 802274 | 197677 | 19.77% |  | 7 | 1.3838 | 1 | 1 | 0.9756% | 0.567 | 900.3296 | 31919.034 | 3000 | 2.927% | 0.5265 | 3430.8189 | 923000 | 46150 | 4.39% | 0.405 | 3430.8189 | 0 | 0
PUD No 1 of Grays Harbor Cnty |  | 0 | Yes | Yes | 1 | 1 | 42953 | 956101 | 466645 | 337185 | 152271 | 803830 | 84.07% |  | 18 | 15.1333 | 22 | 12 | 0.9756% | 0.56525 | 2587.1302 | 475666.3783 | 24500 | 2.927% | 0.52487 | 8558.8258 | 4466000 | 223300 | 4.39% | 0.40375 | 11021.7824 | 210000 | 10500
City of Richland |  | 0 | No | Yes | 1 | 3 | 24527 | 931884 | 338631 | 435831 | 157422 | 774462 | 83.11% |  | 14 | 11.635 | 10 | 10 | 0.9756% | 0.665 | 2719.9811 | 308174.9874 | 16000 | 2.927% | 0.6175 | 9119.0442 | 2930000 | 146500 | 4.39% | 0.475 | 9119.0442 | 0 | 0
PUD No 1 of Lewis County |  | 0 | No | Yes | 1 | 1 | 32385 | 922377 | 437275 | 218423 | 266679 | 655698 | 71.09% |  | 13 | 9.2414 | 13 | 7 | 0.9756% | 0.56525 | 2243.3292 | 281207.104 | 15000 | 2.927% | 0.52487 | 7461.409 | 2915000 | 145750 | 4.39% | 0.40375 | 7461.409 | 0 | 0
Inland Power & Light Company |  | 0 | Yes | Yes | 2 | 2 | 41707 | 915503 | 656947 | 167846 | 90710 | 824793 | 90.09% |  | 17 | 15.3156 | 22 | 12 | 0.9756% | 0.567 | 2940.306 | 476578.0178 | 24250 | 2.927% | 0.5265 | 9531.7293 | 4466000 | 223300 | 4.39% | 0.405 | 11961.2729 | 210000 | 10500
Emerald People's Utility Dist |  | 0 | Yes | Yes | 1 | 1 | 21573 | 790440 | 285445 | 108536 | 396459 | 393981 | 49.84% |  | 12 | 5.9812 | 5 | 5 | 0.9756% | 0.56525 | 1450.6182 | 154905.9511 | 9250 | 2.927% | 0.52487 | 4950.7731 | 1815000 | 90750 | 4.39% | 0.40375 | 6509.1754 | 210000 | 10500
Northern Wasco County PUD |  | 0 | Yes | Yes | 1 | 3 | 10112 | 784410 | 138890 | 19690 | 625830 | 158580 | 20.22% |  | 6 | 1.213 | 1 | 1 | 0.9756% | 0.665 | 884.875 | 31064.9405 | 2750 | 2.927% | 0.6175 | 3317.1498 | 923000 | 46150 | 4.39% | 0.475 | 4665.9018 | 210000 | 10500
City of Springfield |  | 0 | No | Yes | 1 | 2 | 32276 | 765937 | 370238 | 256249 | 139450 | 626487 | 81.79% |  | 13 | 10.6332 | 15 | 8 | 0.9756% | 0.5985 | 2152.4904 | 323165.8021 | 16750 | 2.927% | 0.55575 | 7128.6714 | 3247000 | 162350 | 4.39% | 0.4275 | 7128.6714 | 0 | 0
Central Electric Coop Inc |  | 0 | Yes | Yes | 2 | 1 | 34508 | 721227 | 491376 | 121002 | 108849 | 612378 | 84.91% |  | 14 | 11.8871 | 17 | 9 | 0.9756% | 0.5355 | 2078.2961 | 364435.4621 | 18750 | 2.927% | 0.49725 | 6759.9808 | 3579000 | 178950 | 4.39% | 0.3825 | 8507.1421 | 210000 | 10500
McMinnville City of |  | 0 | No | Yes | 1 | 2 | 16416 | 697188 | 190078 | 174545 | 332565 | 364623 | 52.3% |  | 10 | 5.2299 | 4 | 4 | 0.9756% | 0.5985 | 1281.6708 | 126149.5465 | 7500 | 2.927% | 0.55575 | 4433.9318 | 1592000 | 79600 | 4.39% | 0.4275 | 4433.9318 | 0 | 0
Idaho Falls City of |  | 0 | Yes | Yes | 3 | 1 | 28175 | 684813 | 282284 | 334872 | 67657 | 617156 | 90.12% |  | 12 | 10.8144 | 15 | 8 | 0.9756% | 0.476 | 1555.3843 | 324072.2212 | 16500 | 2.927% | 0.442 | 5175.008 | 3247000 | 162350 | 4.39% | 0.34 | 6732.1963 | 210000 | 10500
Oregon Trail El Cons Coop, Inc |  | 0 | Yes | Yes | 2 | 1 | 31254 | 657478 | 289676 | 250128 | 117674 | 539804 | 82.1% |  | 13 | 10.6733 | 15 | 8 | 0.9756% | 0.5355 | 1612.8116 | 323366.4396 | 16750 | 2.927% | 0.49725 | 5364.0739 | 3247000 | 162350 | 4.39% | 0.3825 | 6951.3731 | 210000 | 10500
PUD No 3 of Mason County |  | 0 | No | Yes | 1 | 1 | 33841 | 645683 | 421592 | 186277 | 37814 | 607869 | 94.14% |  | 14 | 13.1801 | 19 | 10 | 0.9756% | 0.56525 | 2048.7743 | 405900.4961 | 20500 | 2.927% | 0.52487 | 6670.1653 | 3911000 | 195550 | 4.39% | 0.40375 | 6670.1653 | 0 | 0
PUD No 1 of Clallam County |  | 0 | Yes | Yes | 1 | 1 | 31905 | 632220 | 439440 | 172619 | 20161 | 612059 | 96.81% |  | 13 | 12.5854 | 18 | 10 | 0.9756% | 0.56525 | 2082.6769 | 392927.201 | 19750 | 2.927% | 0.52487 | 6757.4855 | 3802000 | 190100 | 4.39% | 0.40375 | 8510.4118 | 210000 | 10500
PUD No 1 of Okanogan County |  | 0 | No | Yes | 1 | 3 | 21114 | 599394 | 290654 | 293747 | 14993 | 584401 | 97.5% |  | 12 | 11.6998 | 10 | 10 | 0.9756% | 0.665 | 2087.1674 | 308499.1842 | 15500 | 2.927% | 0.6175 | 6883.9984 | 2930000 | 146500 | 4.39% | 0.475 | 6883.9984 | 0 | 0
Peninsula Light Company |  | 0 | Yes | Yes | 1 | 1 | 33335 | 581348 | 481481 | 99867 | 0 | 581348 | 100% |  | 14 | 14 | 20 | 11 | 0.9756% | 0.56525 | 2078.9261 | 435000 | 21750 | 2.927% | 0.52487 | 6684.3722 | 4134000 | 206700 | 4.39% | 0.40375 | 8316.4847 | 210000 | 10500
Benton Rural Electric Assn |  | 0 | No | Yes | 1 | 3 | 14424 | 545796 | 208105 | 130729 | 206962 | 338834 | 62.08% |  | 9 | 5.5873 | 5 | 5 | 0.9756% | 0.665 | 1351.4954 | 152936.3169 | 8500 | 2.927% | 0.6175 | 4564.2835 | 1815000 | 90750 | 4.39% | 0.475 | 4564.2835 | 0 | 0
Big Bend Electric Coop, Inc |  | 0 | No | Yes | 1 | 3 | 9349 | 538117 | 103377 | 106379 | 328361 | 209756 | 38.98% |  | 7 | 2.7286 | 1 | 3 | 0.9756% | 0.665 | 852.0664 | 68642.8695 | 4500 | 2.927% | 0.6175 | 3049.4355 | 1151000 | 57550 | 4.39% | 0.475 | 3049.4355 | 0 | 0
Columbia River Peoples Ut Dist |  | 0 | No | Yes | 1 | 1 | 19443 | 482419 | 215305 | 102200 | 164914 | 317505 | 65.82% |  | 11 | 7.2397 | 6 | 6 | 0.9756% | 0.56525 | 1102.0401 | 186198.3566 | 10250 | 2.927% | 0.52487 | 3684.3982 | 2038000 | 101900 | 4.39% | 0.40375 | 3684.3982 | 0 | 0
Tillamook Peoples Utility Dist |  | 0 | No | No | 1 | 1 | 21242 | 469888 | 232930 | 127363 | 109595 | 360293 | 76.68% |  | 12 | 9.2012 | 8 | 8 | 0.9756% | 0.56525 | 1210.3296 | 246005.8142 | 13000 | 2.927% | 0.52487 | 4009.3025 | 2484000 | 124200 | 4.39% | 0.40375 | 4009.3025 | 0 | 0
Kootenai Electric Coop Inc |  | 0 | No | Yes | 2 | 2 | 25548 | 464745 | 321923 | 112601 | 30221 | 434524 | 93.5% |  | 11 | 10.2847 | 15 | 8 | 0.9756% | 0.567 | 1504.0577 | 321423.5118 | 16250 | 2.927% | 0.5265 | 4882.7507 | 3247000 | 162350 | 4.39% | 0.405 | 4882.7507 | 0 | 0
Midstate Electric Coop, Inc |  | 0 | No | Yes | 2 | 1 | 19362 | 404275 | 258677 | 117183 | 28415 | 375860 | 92.97% |  | 11 | 10.2269 | 9 | 9 | 0.9756% | 0.5355 | 1198.3072 | 276134.2527 | 14000 | 2.927% | 0.49725 | 3905.8323 | 2707000 | 135350 | 4.39% | 0.3825 | 3905.8323 | 0 | 0
Consumers Power, Inc |  | 0 | No | Yes | 1 | 2 | 22655 | 401942 | 273091 | 87933 | 40918 | 361024 | 89.82% |  | 13 | 11.6766 | 10 | 10 | 0.9756% | 0.5985 | 1333.5327 | 308382.9508 | 15750 | 2.927% | 0.55575 | 4335.3559 | 2930000 | 146500 | 4.39% | 0.4275 | 4335.3559 | 0 | 0
USBIA-Mission Valley Power |  | 0 | No | Yes | 3 | 2 | 21462 | 380185 | 235022 | 127147 | 18016 | 362169 | 95.26% |  | 12 | 11.4314 | 10 | 10 | 0.9756% | 0.504 | 1063.44 | 307156.7526 | 15500 | 2.927% | 0.468 | 3470.862 | 2930000 | 146500 | 4.39% | 0.36 | 3470.862 | 0 | 0
PUD No 1 of Jefferson County |  | 0 | No | Yes | 1 | 1 | 19877 | 376436 | 207266 | 69200 | 99970 | 276466 | 73.44% |  | 12 | 8.8132 | 7 | 7 | 0.9756% | 0.56525 | 980.3073 | 219065.8173 | 11750 | 2.927% | 0.52487 | 3232.3564 | 2261000 | 113050 | 4.39% | 0.40375 | 3232.3564 | 0 | 0
PUD No 1 of Klickitat County |  | 0 | No | Yes | 1 | 3 | 12710 | 344507 | 141628 | 111719 | 91160 | 253347 | 73.54% |  | 8 | 5.8831 | 5 | 5 | 0.9756% | 0.665 | 962.6942 | 154415.5997 | 8250 | 2.927% | 0.6175 | 3222.0469 | 1815000 | 90750 | 4.39% | 0.475 | 3222.0469 | 0 | 0
Columbia Rural Elec Assn, Inc |  | 0 | No | Yes | 1 | 3 | 5978 | 338669 | 53126 | 72355 | 213188 | 125481 | 37.05% |  | 5 | 1.8526 | 1 | 2 | 0.9756% | 0.665 | 498.1959 | 49262.8053 | 3250 | 2.927% | 0.6175 | 1807.2647 | 1037000 | 51850 | 4.39% | 0.475 | 1807.2647 | 0 | 0
Coos-Curry Electric Coop, Inc |  | 0 | No | Yes | 1 | 1 | 17878 | 328481 | 179106 | 91608 | 57767 | 270714 | 82.41% |  | 10 | 8.2414 | 7 | 7 | 0.9756% | 0.56525 | 909.3949 | 216206.9496 | 11250 | 2.927% | 0.52487 | 2993.5618 | 2261000 | 113050 | 4.39% | 0.40375 | 2993.5618 | 0 | 0
Salem Electric |  | 0 | No | Yes | 1 | 1 | 19822 | 317746 | 182733 | 108802 | 26211 | 291535 | 91.75% |  | 12 | 11.0101 | 9 | 9 | 0.9756% | 0.56525 | 952.6224 | 280050.575 | 14250 | 2.927% | 0.52487 | 3121.7286 | 2707000 | 135350 | 4.39% | 0.40375 | 3121.7286 | 0 | 0
Northern Lights, Inc |  | 0 | No | Yes | 2 | 2 | 20162 | 307997 | 232021 | 47849 | 28127 | 279870 | 90.87% |  | 12 | 10.9041 | 9 | 9 | 0.9756% | 0.567 | 1012.0848 | 279520.6609 | 14250 | 2.927% | 0.5265 | 3272.3233 | 2707000 | 135350 | 4.39% | 0.405 | 3272.3233 | 0 | 0
Fall River Rural Elec Coop Inc |  | 0 | No | Yes | 3 | 1 | 16659 | 299875 | 172199 | 127676 | 0 | 299875 | 100% |  | 10 | 10 | 9 | 9 | 0.9756% | 0.476 | 796.9387 | 275000 | 13750 | 2.927% | 0.442 | 2607.9794 | 2707000 | 135350 | 4.39% | 0.34 | 2607.9794 | 0 | 0
United Electric Co-op, Inc |  | 0 | No | Yes | 2 | 3 | 6736 | 298313 | 89525 | 63886 | 144902 | 153411 | 51.43% |  | 5 | 2.5713 | 1 | 3 | 0.9756% | 0.63 | 586.7728 | 67856.5466 | 4000 | 2.927% | 0.585 | 2021.3011 | 1151000 | 57550 | 4.39% | 0.45 | 2021.3011 | 0 | 0
Pacific Public Utility District No 2 |  | 0 | No | Yes | 1 | 1 | 17496 | 291438 | 178573 | 89854 | 23011 | 268427 | 92.1% |  | 10 | 9.2104 | 8 | 8 | 0.9756% | 0.56525 | 893.885 | 246052.162 | 12500 | 2.927% | 0.52487 | 2920.1459 | 2484000 | 124200 | 4.39% | 0.40375 | 2920.1459 | 0 | 0
Elmhurst Mutual Power & Light Co |  | 0 | No | Yes | 1 | 1 | 15462 | 271244 | 229819 | 41425 | 0 | 271244 | 100% |  | 9 | 9 | 8 | 8 | 0.9756% | 0.56525 | 978.5349 | 245000 | 12250 | 2.927% | 0.52487 | 3142.6089 | 2484000 | 124200 | 4.39% | 0.40375 | 3142.6089 | 0 | 0
Port Angeles City of |  | 0 | No | Yes | 1 | 1 | 10971 | 268893 | 123274 | 101550 | 44069 | 224824 | 83.61% |  | 7 | 5.8528 | 5 | 5 | 0.9756% | 0.56525 | 712.0234 | 154263.8336 | 8000 | 2.927% | 0.52487 | 2362.7225 | 1815000 | 90750 | 4.39% | 0.40375 | 2362.7225 | 0 | 0
City of Centralia |  | 0 | No | Yes | 1 | 1 | 10282 | 260526 | 115021 | 33489 | 112016 | 148510 | 57% |  | 6 | 3.4202 | 3 | 3 | 0.9756% | 0.56525 | 548.7673 | 92101.1722 | 5250 | 2.927% | 0.52487 | 1842.8935 | 1369000 | 68450 | 4.39% | 0.40375 | 1842.8935 | 0 | 0
Lakeview Light & Power |  | 0 | No | Yes | 1 | 1 | 10097 | 257169 | 106703 | 89895 | 60571 | 196598 | 76.45% |  | 6 | 4.5868 | 4 | 4 | 0.9756% | 0.56525 | 626.8962 | 122934.1017 | 6500 | 2.927% | 0.52487 | 2094.8965 | 1592000 | 79600 | 4.39% | 0.40375 | 2094.8965 | 0 | 0
City of Forest Grove |  | 0 | No | Yes | 1 | 1 | 10126 | 246903 | 112058 | 24199 | 110646 | 136257 | 55.19% |  | 6 | 3.3112 | 3 | 3 | 0.9756% | 0.56525 | 516.4593 | 91555.9349 | 5250 | 2.927% | 0.52487 | 1733.0169 | 1369000 | 68450 | 4.39% | 0.40375 | 1733.0169 | 0 | 0
Lane Electric Coop Inc |  | 0 | No | Yes | 1 | 1 | 12850 | 231436 | 185955 | 41125 | 4356 | 227080 | 98.12% |  | 8 | 7.8494 | 7 | 7 | 0.9756% | 0.56525 | 809.7485 | 214247.1353 | 10750 | 2.927% | 0.52487 | 2607.9185 | 2261000 | 113050 | 4.39% | 0.40375 | 2607.9185 | 0 | 0
Missoula Electric Coop, Inc |  | 0 | No | Yes | 2 | 3 | 15084 | 229182 | 164982 | 46587 | 17613 | 211569 | 92.31% |  | 9 | 8.3083 | 7 | 7 | 0.9756% | 0.63 | 829.7736 | 216541.6787 | 11000 | 2.927% | 0.585 | 2688.8381 | 2261000 | 113050 | 4.39% | 0.45 | 2688.8381 | 0 | 0
Modern Electric Water Company |  | 0 | No | Yes | 2 | 2 | 10020 | 222686 | 96035 | 126651 | 0 | 222686 | 100% |  | 6 | 6 | 5 | 5 | 0.9756% | 0.567 | 652.1048 | 155000 | 7750 | 2.927% | 0.5265 | 2159.7313 | 1815000 | 90750 | 4.39% | 0.405 | 2159.7313 | 0 | 0
Vera Irrigation District #15 |  | 0 | No | Yes | 2 | 2 | 11897 | 220910 | 142882 | 78028 | 0 | 220910 | 100% |  | 7 | 7 | 6 | 6 | 0.9756% | 0.567 | 725.9182 | 185000 | 9250 | 2.927% | 0.5265 | 2362.6176 | 2038000 | 101900 | 4.39% | 0.405 | 2362.6176 | 0 | 0
PUD No 1 of Whatcom County |  | 0 | No | Yes | 1 | 2 | 1 | 220310 | 0 | 0 | 220310 | 0 | 0% |  | 1 | 0 | 0 | 0 | 0.9756% | 0.5985 | 64.3198 | 0 | 250 | 2.927% | 0.55575 | 358.353 | 700000 | 35000 | 4.39% | 0.4275 | 358.353 | 0 | 0
Raft River Rural Elec Coop Inc |  | 0 | No | Yes | 2 | 3 | 2616 | 219252 | 23537 | 47758 | 147957 | 71295 | 32.52% |  | 2 | 0.65035 | 0 | 1 | 0.9756% | 0.63 | 264.151 | 18251.7377 | 1250 | 2.927% | 0.585 | 984.5858 | 814000 | 40700 | 4.39% | 0.45 | 984.5858 | 0 | 0
Orcas Power & Light Coop |  | 0 | No | Yes | 1 | 1 | 15082 | 208733 | 149472 | 59261 | 0 | 208733 | 100% |  | 9 | 9 | 8 | 8 | 0.9756% | 0.56525 | 707.7195 | 245000 | 12250 | 2.927% | 0.52487 | 2292.1639 | 2484000 | 124200 | 4.39% | 0.40375 | 2292.1639 | 0 | 0
City of Ellensburg |  | 0 | No | Yes | 2 | 2 | 9774 | 205282 | 76934 | 120212 | 8136 | 197146 | 96.04% |  | 7 | 6.7226 | 3 | 7 | 0.9756% | 0.567 | 566.1448 | 168612.835 | 8500 | 2.927% | 0.5265 | 1887.1835 | 1825000 | 91250 | 4.39% | 0.405 | 1887.1835 | 0 | 0
Clearwater Power Company |  | 0 | No | Yes | 1 | 3 | 10754 | 189153 | 129142 | 30522 | 29489 | 159664 | 84.41% |  | 6 | 5.0646 | 4 | 4 | 0.9756% | 0.665 | 675.2679 | 125322.9925 | 6500 | 2.927% | 0.6175 | 2196.315 | 1592000 | 79600 | 4.39% | 0.475 | 2196.315 | 0 | 0
Canby Utility Board |  | 0 | No | Yes | 1 | 2 | 7462 | 185047 | 76959 | 72556 | 35532 | 149515 | 80.8% |  | 6 | 4.8479 | 2 | 5 | 0.9756% | 0.5985 | 494.3919 | 119239.5175 | 6250 | 2.927% | 0.55575 | 1649.3315 | 1488000 | 74400 | 4.39% | 0.4275 | 1649.3315 | 0 | 0
City of Ashland |  | 0 | No | Yes | 1 | 3 | 11978 | 171916 | 86287 | 85629 | 0 | 171916 | 100% |  | 7 | 7 | 6 | 6 | 0.9756% | 0.665 | 614.087 | 185000 | 9250 | 2.927% | 0.6175 | 2021.3775 | 2038000 | 101900 | 4.39% | 0.475 | 2021.3775 | 0 | 0
Blachly-Lane Cnty Coop El Assn |  | 0 | No | Yes | 1 | 2 | 3616 | 171676 | 49387 | 10817 | 111472 | 60204 | 35.07% |  | 3 | 1.0521 | 0 | 1 | 0.9756% | 0.5985 | 259.669 | 20260.2577 | 1500 | 2.927% | 0.55575 | 911.95 | 814000 | 40700 | 4.39% | 0.4275 | 911.95 | 0 | 0
Glacier Electric Coop, Inc |  | 0 | No | Yes | 3 | 3 | 7728 | 170470 | 70883 | 79672 | 19915 | 150555 | 88.32% |  | 6 | 5.2991 | 2 | 6 | 0.9756% | 0.56 | 450.6369 | 136495.2778 | 7000 | 2.927% | 0.52 | 1499.6379 | 1602000 | 80100 | 4.39% | 0.4 | 1499.6379 | 0 | 0
Vigilante Electric Coop, Inc |  | 0 | No | Yes | 3 | 3 | 10060 | 166498 | 109302 | 7713 | 49483 | 117015 | 70.28% |  | 6 | 4.2168 | 4 | 4 | 0.9756% | 0.56 | 448.3865 | 121084.037 | 6500 | 2.927% | 0.52 | 1464.8233 | 1592000 | 79600 | 4.39% | 0.4 | 1464.8233 | 0 | 0
Ravalli County Elec Coop, Inc |  | 0 | No | Yes | 2 | 3 | 10552 | 154006 | 132071 | 12293 | 9642 | 144364 | 93.74% |  | 6 | 5.6244 | 5 | 5 | 0.9756% | 0.63 | 601.4134 | 153121.7615 | 7750 | 2.927% | 0.585 | 1930.7996 | 1815000 | 90750 | 4.39% | 0.45 | 1930.7996 | 0 | 0
Douglas Electric Coop, Inc |  | 0 | Yes | Yes | 1 | 2 | 10087 | 151034 | 125093 | 18752 | 7189 | 143845 | 95.24% |  | 6 | 5.7144 | 5 | 5 | 0.9756% | 0.5985 | 557.1909 | 153572.0434 | 7750 | 2.927% | 0.55575 | 1791.9977 | 1815000 | 90750 | 4.39% | 0.4275 | 2227.0193 | 210000 | 10500
City of Cheney |  | 0 | No | Yes | 2 | 2 | 5676 | 139677 | 57860 | 67246 | 14571 | 125106 | 89.57% |  | 5 | 4.4784 | 2 | 5 | 0.9756% | 0.567 | 376.8694 | 117392.0187 | 6000 | 2.927% | 0.5265 | 1253.8626 | 1488000 | 74400 | 4.39% | 0.405 | 1253.8626 | 0 | 0
WAPA-- Western Area Power Administration |  | 0 | No | No | 1 | 2 | 15 | 122801 | 0 | 96630 | 26171 | 96630 | 78.69% |  | 1 | 0.78688 | 0 | 1 | 0.9756% | 0.5985 | 233.3306 | 18934.4142 | 1000 | 2.927% | 0.55575 | 828.4541 | 814000 | 40700 | 4.39% | 0.4275 | 828.4541 | 0 | 0
PUD No 1 of Skamania Co |  | 0 | No | Yes | 1 | 2 | 6101 | 120564 | 75435 | 28718 | 16411 | 104153 | 86.39% |  | 5 | 4.3194 | 2 | 5 | 0.9756% | 0.5985 | 380.192 | 116597.0356 | 6000 | 2.927% | 0.55575 | 1241.867 | 1488000 | 74400 | 4.39% | 0.4275 | 1241.867 | 0 | 0
Hood River Electric Coop |  | 0 | No | Yes | 1 | 3 | 3865 | 118389 | 52252 | 6434 | 59703 | 58686 | 49.57% |  | 3 | 1.4871 | 1 | 2 | 0.9756% | 0.665 | 273.3646 | 47435.5726 | 2750 | 2.927% | 0.6175 | 921.5311 | 1037000 | 51850 | 4.39% | 0.475 | 921.5311 | 0 | 0
Lincoln Electric Coop, Inc |  | 0 | No | Yes | 3 | 3 | 5887 | 117955 | 81687 | 29465 | 6803 | 111152 | 94.23% |  | 5 | 4.7116 | 2 | 5 | 0.9756% | 0.56 | 378.6532 | 118558.1366 | 6000 | 2.927% | 0.52 | 1229.1643 | 1488000 | 74400 | 4.39% | 0.4 | 1229.1643 | 0 | 0
City of Burley |  | 0 | No | Yes | 2 | 3 | 4768 | 115765 | 46306 | 69459 | 0 | 115765 | 100% |  | 4 | 4 | 2 | 4 | 0.9756% | 0.63 | 369.9962 | 100000 | 5000 | 2.927% | 0.585 | 1228.9161 | 1374000 | 68700 | 4.39% | 0.45 | 1228.9161 | 0 | 0
Parkland Light & Water Company |  | 0 | No | Yes | 1 | 1 | 4566 | 113395 | 54913 | 58482 | 0 | 113395 | 100% |  | 4 | 4 | 2 | 4 | 0.9756% | 0.56525 | 340.9803 | 100000 | 5000 | 2.927% | 0.52487 | 1124.0733 | 1374000 | 68700 | 4.39% | 0.40375 | 1124.0733 | 0 | 0
Columbia Basin Elec Cooperative, Inc |  | 0 | No | Yes | 1 | 3 | 3890 | 108960 | 39961 | 27108 | 41891 | 67069 | 61.55% |  | 3 | 1.8466 | 1 | 2 | 0.9756% | 0.665 | 265.419 | 49233.0672 | 2750 | 2.927% | 0.6175 | 898.4517 | 1037000 | 51850 | 4.39% | 0.475 | 898.4517 | 0 | 0
City of Hermiston |  | 0 | No | Yes | 1 | 2 | 5366 | 107121 | 51860 | 55261 | 0 | 107121 | 100% |  | 4 | 4 | 2 | 4 | 0.9756% | 0.5985 | 341.0364 | 100000 | 5000 | 2.927% | 0.55575 | 1124.2714 | 1374000 | 68700 | 4.39% | 0.4275 | 1124.2714 | 0 | 0
Wasco Electric Coop, Inc |  | 0 | No | Yes | 1 | 3 | 4704 | 106704 | 49822 | 17192 | 39690 | 67014 | 62.8% |  | 4 | 2.5121 | 1 | 3 | 0.9756% | 0.665 | 283.7552 | 67560.7287 | 3750 | 2.927% | 0.6175 | 947.4426 | 1151000 | 57550 | 4.39% | 0.475 | 947.4426 | 0 | 0
City of Milton-Freewater |  | 0 | No | Yes | 1 | 3 | 4408 | 103892 | 58599 | 14301 | 30992 | 72900 | 70.17% |  | 4 | 2.8068 | 1 | 3 | 0.9756% | 0.665 | 313.2916 | 69033.8043 | 3750 | 2.927% | 0.6175 | 1032.5004 | 1151000 | 57550 | 4.39% | 0.475 | 1032.5004 | 0 | 0
Harney Electric Coop, Inc |  | 0 | No | Yes | 2 | 1 | 3682 | 217597 | 30166 | 0 | 187431 | 30166 | 13.86% |  | 3 | 0.4159 | 0 | 0 | 0.9756% | 0.5355 | 159.2799 | 2079.4864 | 750 | 2.927% | 0.49725 | 624.0012 | 700000 | 35000 | 4.39% | 0.3825 | 624.0012 | 0 | 0
Salmon River Electric Coop Inc |  | 0 | No | Yes | 2 | 2 | 2797 | 98091 | 31663 | 21865 | 44563 | 53528 | 54.57% |  | 2 | 1.0914 | 0 | 1 | 0.9756% | 0.567 | 183.3111 | 20456.9736 | 1250 | 2.927% | 0.5265 | 627.4729 | 814000 | 40700 | 4.39% | 0.405 | 627.4729 | 0 | 0
PUD No 1 of Kittitas County |  | 0 | No | Yes | 3 | 1 | 4485 | 97901 | 59494.851 | 31191.6214 | 7214.5276 | 90686.4724 | 92.63% |  | 4 | 3.7052 | 2 | 4 | 0.9756% | 0.476 | 253.0173 | 98526.1585 | 5000 | 2.927% | 0.442 | 826.8178 | 1374000 | 68700 | 4.39% | 0.34 | 826.8178 | 0 | 0
Tanner Electric Coop |  | 0 | No | Yes | 1 | 1 | 4911 | 90680 | 58091 | 32589 | 0 | 90680 | 100% |  | 4 | 4 | 2 | 4 | 0.9756% | 0.56525 | 296.132 | 100000 | 5000 | 2.927% | 0.52487 | 964.2435 | 1374000 | 68700 | 4.39% | 0.40375 | 964.2435 | 0 | 0
Ohop Mutual Light Company, Inc |  | 0 | No | Yes | 1 | 1 | 4413 | 82179 | 77776 | 4358 | 45 | 82134 | 99.95% |  | 4 | 3.9978 | 2 | 4 | 0.9756% | 0.56525 | 309.8598 | 99989.0483 | 5000 | 2.927% | 0.52487 | 989.3914 | 1374000 | 68700 | 4.39% | 0.40375 | 989.3914 | 0 | 0
Rupert City of |  | 0 | No | Yes | 2 | 3 | 3012 | 77418 | 35718 | 28569 | 13131 | 64287 | 83.04% |  | 3 | 2.4912 | 1 | 3 | 0.9756% | 0.63 | 227.9478 | 67455.8242 | 3500 | 2.927% | 0.585 | 756.3108 | 1151000 | 57550 | 4.39% | 0.45 | 756.3108 | 0 | 0
City of Bonners Ferry |  | 0 | No | Yes | 2 | 2 | 2767 | 77390 | 26446.0485 | 27999.376 | 22944.5755 | 54445.4245 | 70.35% |  | 2 | 1.407 | 1 | 1 | 0.9756% | 0.567 | 170.7041 | 32035.2015 | 1750 | 2.927% | 0.5265 | 577.1105 | 923000 | 46150 | 4.39% | 0.405 | 577.1105 | 0 | 0
City of Blaine |  | 0 | No | Yes | 1 | 1 | 3395 | 76758 | 26502 | 38836 | 11420 | 65338 | 85.12% |  | 3 | 2.5537 | 1 | 3 | 0.9756% | 0.56525 | 191.1196 | 67768.3108 | 3500 | 2.927% | 0.52487 | 641.5498 | 1151000 | 57550 | 4.39% | 0.40375 | 641.5498 | 0 | 0
PUD No 1 of Mason County |  | 0 | No | Yes | 1 | 1 | 5293 | 75659 | 59641.3137 | 16017.6863 | 0 | 75659 | 100% |  | 4 | 4 | 2 | 4 | 0.9756% | 0.56525 | 265.5627 | 100000 | 5000 | 2.927% | 0.52487 | 856.0106 | 1374000 | 68700 | 4.39% | 0.40375 | 856.0106 | 0 | 0
Lost River Electric Coop Inc |  | 0 | No | Yes | 2 | 3 | 2728 | 73841 | 27149.6098 | 5660.9651 | 0 | 32810.575 | 44.43% |  | 2 | 0.88868 | 0 | 1 | 0.9756% | 0.63 | 130.7272 | 19443.4088 | 1250 | 2.927% | 0.585 | 420.3468 | 814000 | 40700 | 4.39% | 0.45 | 420.3468 | 0 | 0
City of Monmouth |  | 0 | No | Yes | 1 | 1 | 4596 | 71954 | 44181 | 27773 | 0 | 71954 | 100% |  | 4 | 4 | 2 | 4 | 0.9756% | 0.56525 | 231.8126 | 100000 | 5000 | 2.927% | 0.52487 | 756.3008 | 1374000 | 68700 | 4.39% | 0.40375 | 756.3008 | 0 | 0
Lower Valley Energy Inc |  | 0 | No | Yes | 3 | 1 | 28129 | 793651 | 463238 | 250390 | 80023 | 713628 | 89.92% |  | 12 | 10.7901 | 15 | 8 | 0.9756% | 0.476 | 1989.5581 | 323950.2628 | 16500 | 2.927% | 0.442 | 6517.2926 | 3247000 | 162350 | 4.39% | 0.34 | 6517.2926 | 0 | 0
PUD No 1 of Ferry County |  | 0 | No | Yes | 2 | 2 | 3507 | 66726 | 35666 | 10165 | 20895 | 45831 | 68.69% |  | 3 | 2.0606 | 1 | 2 | 0.9756% | 0.567 | 166.3769 | 50302.8055 | 2750 | 2.927% | 0.5265 | 550.2023 | 1037000 | 51850 | 4.39% | 0.405 | 550.2023 | 0 | 0
West Oregon Electric Coop Inc |  | 0 | No | Yes | 1 | 1 | 4390 | 64678 | 50619.7344 | 5044.7466 | 9013.519 | 55664.481 | 86.06% |  | 4 | 3.4426 | 2 | 4 | 0.9756% | 0.56525 | 209.0178 | 97212.8022 | 5000 | 2.927% | 0.52487 | 674.7001 | 1374000 | 68700 | 4.39% | 0.40375 | 674.7001 | 0 | 0
City of Heyburn |  | 0 | No | Yes | 2 | 3 | 1664 | 62071 | 30693.6774 | 10571.2641 | 20806.0585 | 41264.9415 | 66.48% |  | 2 | 1.3296 | 1 | 1 | 0.9756% | 0.63 | 164.4416 | 31648.0227 | 1750 | 2.927% | 0.585 | 546.5529 | 923000 | 46150 | 4.39% | 0.45 | 546.5529 | 0 | 0
Nespelem Valley Elec Coop, Inc |  | 0 | No | Yes | 1 | 3 | 1524 | 60886 | 17713.296 | 23299.5732 | 19747.8215 | 41012.8692 | 67.36% |  | 2 | 1.3472 | 1 | 1 | 0.9756% | 0.665 | 147.3155 | 31736.0098 | 1750 | 2.927% | 0.6175 | 502.3475 | 923000 | 46150 | 4.39% | 0.475 | 502.3475 | 0 | 0
City of Bandon |  | 0 | No | Yes | 1 | 1 | 3777 | 60353 | 34708 | 24096 | 1549 | 58804 | 97.43% |  | 3 | 2.923 | 1 | 3 | 0.9756% | 0.56525 | 187.5607 | 69615.015 | 3500 | 2.927% | 0.52487 | 614.0162 | 1151000 | 57550 | 4.39% | 0.40375 | 614.0162 | 0 | 0
South Side Electric, Inc |  | 0 | No | Yes | 1 | 2 | 813 | 58794 | 24232.3489 | 0 | 0 | 24232.3489 | 41.22% |  | 1 | 0.41216 | 0 | 0 | 0.9756% | 0.5985 | 99.0453 | 2060.7842 | 250 | 2.927% | 0.55575 | 315.3279 | 700000 | 35000 | 4.39% | 0.4275 | 315.3279 | 0 | 0
Okanogan County Elec Coop, Inc |  | 0 | Yes | Yes | 1 | 3 | 3574 | 58020 | 38314 | 19706 | 0 | 58020 | 100% |  | 3 | 3 | 1 | 3 | 0.9756% | 0.665 | 225.1411 | 70000 | 3500 | 2.927% | 0.6175 | 732.0393 | 1151000 | 57550 | 4.39% | 0.475 | 925.7043 | 210000 | 10500
Idaho Cnty L&P Coop Assn, Inc |  | 0 | No | Yes | 1 | 3 | 4003 | 51784 | 42956.7001 | 8617.3969 | 209.903 | 51574.097 | 99.59% |  | 3 | 2.9878 | 1 | 3 | 0.9756% | 0.665 | 217.5176 | 69939.1985 | 3500 | 2.927% | 0.6175 | 699.3422 | 1151000 | 57550 | 4.39% | 0.475 | 699.3422 | 0 | 0
City of Weiser |  | 0 | No | Yes | 1 | 3 | 3482 | 48289 | 24693.4239 | 13947.9396 | 9647.6365 | 38641.3635 | 80.02% |  | 3 | 2.4006 | 1 | 3 | 0.9756% | 0.665 | 151.4705 | 67003.1571 | 3500 | 2.927% | 0.6175 | 500.5089 | 1151000 | 57550 | 4.39% | 0.475 | 500.5089 | 0 | 0
PUD No 1 of Wahkiakum County |  | 0 | No | Yes | 1 | 1 | 2539 | 41044 | 29739.8738 | 11304.1262 | 0 | 41044 | 100% |  | 2 | 2 | 1 | 2 | 0.9756% | 0.56525 | 139.7384 | 50000 | 2500 | 2.927% | 0.52487 | 452.3239 | 1037000 | 51850 | 4.39% | 0.40375 | 452.3239 | 0 | 0
Surprise Valley Electrification Corp. |  | 0 | No | Yes | 2 | 2 | 6610 | 135130 | 50059 | 14920 | 70151 | 64979 | 48.09% |  | 5 | 2.4043 | 1 | 3 | 0.9756% | 0.567 | 246.2542 | 67021.5718 | 4000 | 2.927% | 0.5265 | 840.1753 | 1151000 | 57550 | 4.39% | 0.405 | 840.1753 | 0 | 0
Town of Steilacoom |  | 0 | No | Yes | 1 | 1 | 2963 | 37015 | 30709 | 6306 | 0 | 37015 | 100% |  | 3 | 3 | 1 | 3 | 0.9756% | 0.56525 | 132.4543 | 70000 | 3500 | 2.927% | 0.52487 | 425.8431 | 1151000 | 57550 | 4.39% | 0.40375 | 425.8431 | 0 | 0
City of Plummer |  | 0 | No | Yes | 2 | 2 | 963 | 33046 | 10182.5212 | 8809.5158 | 14053.963 | 18992.037 | 57.47% |  | 1 | 0.57472 | 0 | 1 | 0.9756% | 0.567 | 62.8085 | 17873.5758 | 1000 | 2.927% | 0.5265 | 215.0612 | 814000 | 40700 | 4.39% | 0.405 | 215.0612 | 0 | 0
City of Milton |  | 0 | No | Yes | 1 | 1 | 3512 | 33000 | 23109.7535 | 9890.2465 | 0 | 33000 | 100% |  | 3 | 3 | 1 | 3 | 0.9756% | 0.56525 | 111.0257 | 70000 | 3500 | 2.927% | 0.52487 | 359.9812 | 1151000 | 57550 | 4.39% | 0.40375 | 359.9812 | 0 | 0
City of Sumas |  | 0 | No | Yes | 1 | 1 | 900 | 32871 | 6144.1537 | 5377.8004 | 21349.0459 | 11521.9541 | 35.05% |  | 1 | 0.35052 | 0 | 0 | 0.9756% | 0.56525 | 41.4672 | 1752.6017 | 250 | 2.927% | 0.52487 | 149.6144 | 700000 | 35000 | 4.39% | 0.40375 | 149.6144 | 0 | 0
City of McCleary |  | 0 | No | Yes | 1 | 1 | 1119 | 31802 | 16771.8821 | 4615.2841 | 10414.8338 | 21387.1662 | 67.25% |  | 1 | 0.67251 | 0 | 1 | 0.9756% | 0.56525 | 77.7959 | 18362.5505 | 1000 | 2.927% | 0.52487 | 257.5723 | 814000 | 40700 | 4.39% | 0.40375 | 257.5723 | 0 | 0
Town of Eatonville |  | 0 | No | Yes | 1 | 1 | 1231 | 26769 | 16229.4389 | 10539.5686 | 0 | 26769.0074 | 100% |  | 1 | 1 | 0 | 1 | 0.9756% | 0.56525 | 85.8983 | 20000.0014 | 1000 | 2.927% | 0.52487 | 280.4113 | 814000 | 40700 | 4.39% | 0.40375 | 280.4113 | 0 | 0
City of Soda Springs |  | 0 | No | Yes | 3 | 1 | 1871 | 26496 | 11797.9554 | 13965.6271 | 397.5642 | 25763.5825 | 97.24% |  | 2 | 1.9447 | 1 | 2 | 0.9756% | 0.476 | 64.3863 | 49723.5743 | 2500 | 2.927% | 0.442 | 212.9483 | 1037000 | 51850 | 4.39% | 0.34 | 212.9483 | 0 | 0
East End Mutual Elec Co Ltd |  | 0 | No | Yes | 2 | 3 | 747 | 24404 | 15232.1858 | 9171.8142 | 0 | 24404 | 100% |  | 1 | 1 | 0 | 1 | 0.9756% | 0.63 | 88.0848 | 20000 | 1000 | 2.927% | 0.585 | 287.1635 | 814000 | 40700 | 4.39% | 0.45 | 287.1635 | 0 | 0
Columbia Power Coop Assn Inc |  | 0 | No | Yes | 1 | 3 | 1894 | 23378 | 13579 | 4549 | 5250 | 18128 | 77.54% |  | 2 | 1.5509 | 1 | 2 | 0.9756% | 0.665 | 75.1768 | 47754.2989 | 2500 | 2.927% | 0.6175 | 246.9283 | 1037000 | 51850 | 4.39% | 0.475 | 246.9283 | 0 | 0
City of Cascade Locks |  | 0 | No | Yes | 1 | 2 | 911 | 22149 | 10091.8732 | 12057.1268 | 0 | 22149 | 100% |  | 1 | 1 | 0 | 1 | 0.9756% | 0.5985 | 69.4094 | 20000 | 1000 | 2.927% | 0.55575 | 229.3821 | 814000 | 40700 | 4.39% | 0.4275 | 229.3821 | 0 | 0
City of Chewelah |  | 0 | No | Yes | 2 | 2 | 1293 | 21475 | 11436.6981 | 10396.9983 | 0 | 21833.6964 | 101.7% |  | 1 | 1.0167 | 0 | 1 | 0.9756% | 0.567 | 67.2904 | 20083.5149 | 1000 | 2.927% | 0.5265 | 221.097 | 814000 | 40700 | 4.39% | 0.405 | 221.097 | 0 | 0
Riverside Electric Cooperative |  | 0 | No | Yes | 2 | 3 | 594 | 21311 | 14844.7995 | 0 | 0 | 14844.7995 | 69.66% |  | 1 | 0.69658 | 0 | 1 | 0.9756% | 0.63 | 63.8688 | 18482.896 | 1000 | 2.927% | 0.585 | 203.3375 | 814000 | 40700 | 4.39% | 0.45 | 203.3375 | 0 | 0
City of Coulee Dam |  | 0 | No | Yes | 1 | 2 | 597 | 16437 | 9334.616 | 7102.384 | 0 | 16437 | 100% |  | 1 | 1 | 0 | 1 | 0.9756% | 0.5985 | 54.7419 | 20000 | 1000 | 2.927% | 0.55575 | 179.2316 | 814000 | 40700 | 4.39% | 0.4275 | 179.2316 | 0 | 0
City of Troy |  | 0 | No | Yes | 2 | 2 | 978 | 16371 | 11318.4437 | 4989.2931 | 63.2632 | 16307.7368 | 99.61% |  | 1 | 0.99614 | 0 | 1 | 0.9756% | 0.567 | 54.8844 | 19980.6783 | 1000 | 2.927% | 0.5265 | 178.0709 | 814000 | 40700 | 4.39% | 0.405 | 178.0709 | 0 | 0
City of Drain |  | 0 | No | Yes | 1 | 1 | 753 | 15996 | 7592.5452 | 3513.3088 | 4890.146 | 11105.854 | 69.43% |  | 1 | 0.69429 | 0 | 1 | 0.9756% | 0.56525 | 38.4073 | 18471.4472 | 1000 | 2.927% | 0.52487 | 127.8089 | 814000 | 40700 | 4.39% | 0.40375 | 127.8089 | 0 | 0
Town of Ruston |  | 0 | No | Yes | 1 | 1 | 547 | 7475 | 7475 | 0 | 0 | 7475 | 100% |  | 1 | 1 | 0 | 1 | 0.9756% | 0.56525 | 28.8553 | 20000 | 1000 | 2.927% | 0.52487 | 91.8659 | 814000 | 40700 | 4.39% | 0.40375 | 91.8659 | 0 | 0
Alder Mutual Light Co, Inc |  | 0 | No | Yes | 1 | 1 | 292 | 5101 | 4628.0985 | 472.9015 | 0 | 5101 | 100% |  | 1 | 1 | 0 | 1 | 0.9756% | 0.56525 | 18.9087 | 20000 | 1000 | 2.927% | 0.52487 | 60.5106 | 814000 | 40700 | 4.39% | 0.40375 | 60.5106 | 0 | 0
Farmers Electric Company, Ltd |  | 0 | No | Yes | 2 | 3 | 125 | 3803 | 1801.7107 | 1827.7997 | 0 | 3629.5104 | 95.44% |  | 1 | 0.95438 | 0 | 1 | 0.9756% | 0.63 | 12.2455 | 19771.9043 | 1000 | 2.927% | 0.585 | 40.3268 | 814000 | 40700 | 4.39% | 0.45 | 40.3268 | 0 | 0
City of Albion |  | 0 | No | Yes | 2 | 3 | 214 | 2918 | 2011.3514 | 906.6486 | 0 | 2918 | 100% |  | 1 | 1 | 0 | 1 | 0.9756% | 0.63 | 10.8827 | 20000 | 1000 | 2.927% | 0.585 | 35.3124 | 814000 | 40700 | 4.39% | 0.45 | 35.3124 | 0 | 0
City of Minidoka |  | 0 | No | Yes | 2 | 3 | 45 | 811 | 773.473 | 37.527 | 0 | 811 | 100% |  | 1 | 1 | 0 | 1 | 0.9756% | 0.63 | 3.4201 | 20000 | 1000 | 2.927% | 0.585 | 10.916 | 814000 | 40700 | 4.39% | 0.45 | 10.916 | 0 | 0
City of Declo |  | 0 | No | Yes | 2 | 3 | 130 | 273 | 144.1277 | 87.3053 | 32.1599 | 231.433 | 84.77% |  | 1 | 0.84774 | 0 | 1 | 0.9756% | 0.63 | 0.84463 | 19238.6997 | 1000 | 2.927% | 0.585 | 2.7767 | 814000 | 40700 | 4.39% | 0.45 | 2.7767 | 0 | 0
PUD No 1 of Asotin County |  | 0 | No | Yes | 1 | 3 | 3 | 247 | 0 | 0.22469 | 0 | 0.22469 | 0.09097% |  | 1 | 0.00090968 | 0 | 0 | 0.9756% | 0.665 | 0.0005831 | 4.5484 | 250 | 2.927% | 0.6175 | 0.0020304 | 700000 | 35000 | 4.39% | 0.475 | 0.0020304 | 0 | 0
Wells Rural Electric Co. |  |  | Yes | Yes | 1 | 2 | 6136 | 791962 | 59432 | 65167 | 667363 | 124599 | 15.73% |  | 5 | 0.78665 | 0 | 1 | 0.9756% | 0.5985 | 589.9596 | 18933.238 | 2000 | 2.927% | 0.55575 | 2388.8911 | 814000 | 40700 | 4.39% | 0.4275 | 3560.7552 | 210000 | 10500
All Region | [6 empty] | 6679777.9457 | 171684019.4981 | 65586585.9118 | 54773407.3825 | 51241436.7965 | 120359993.2943 | 75.21% |  | 2215 | 1707.3584 | 2731 | 1513 |  |  | 264358.6477 | 39469099.6344 | 3053500 |  |  | 1363937.5471 | 563961000 | 28198050 |  |  | 1676177.058 | 5460000 | 273000
BPA Family | [6 empty] | 2615070 | 69832176 | 27727371.505 | 19847954.0701 | 22174261.0176 | 47575325.5752 | 76.32% |  | 1232 | 933.5758 | 1789 | 802 |  |  | 122639.8682 | 17946255.6159 | 1803500 |  |  | 822931.1969 | 295529000 | 14776450 |  |  | 1058040.5763 | 1470000 | 73500
Delta Between Region and BPA Family | [6 empty] | -60.85% | -59.33% | -57.72% | -63.76% | -56.73% | -60.47% | 1.475% |  | -44.38% | -45.32% | -34.49% | -46.99% |  |  | -53.61% | -54.53% | -40.94% |  |  | -39.67% | -47.6% | -47.6% |  |  | -36.88% | -73.08% | -73.08%
19598.6324
[8 empty] | 40.67% | 42.28% | 36.24% | 43.27% | 39.53% | 101.5%
[8 empty] | 7971.7096 | 3165.2251 | 2265.7482 | 2531.3083
[8 empty] | 19598.6324 | 7487.0532 | 6252.6721 | 5849.4791
SubTotal SUM (Dynamic) | [6 empty] | 2615070 | 69832176
Power Marketer | [6 empty] | 0 | 0
Puget Sound Energy Inc | [6 empty] | 1149781 | 22725923
PacifiCorp | [6 empty] | 798332 | 20852804
Portland General Electric Company | [6 empty] | 888123 | 19221496
NorthWestern Corporation | [6 empty] | 112016.9457 | 3037016.4981
Delivery and Energy Only from EIA
Power Marketer | [7 empty] | 5679853
Puget Sound Energy Inc | [7 empty] | 2028727
PacifiCorp | [7 empty] | 393021
Portland General Electric Company | [7 empty] | 2035494
NorthWestern Corporation | [7 empty] | 1225920.4611
Sum of Delivery Only | [7 empty] | 5683162.4611
Difference | [7 empty] | 3309.4611
Difference (%) | [7 empty] | 0.05823%
NOTE ON DELETIONS
The following EIA-reported reatil sellers were deleted:
EIA Reporting Utility |  | Reason for Deletion
Avangrid Renewables |  | Behind the Meter
BP Energy Company |  | Power Marketer covered under "Delivery" by IOU or POU
Calpine Energy Solutions, LLC |  | Power Marketer covered under "Delivery" by IOU or POU
Constellation NewEnergy, Inc |  | Power Marketer covered under "Delivery" by IOU or POU
Longroad Energy |  | Behind the Meter
Shell Energy North America (US), L.P. |  | Power Marketer covered under "Delivery" by IOU or POU
SolarCity Corporation |  | Behind the Meter
Talen Energy Marketing, LLC |  | Power Marketer covered under "Delivery" by IOU or POU
Tenaska Power Services Co |  | Power Marketer covered under "Delivery" by IOU or POU
Town of Rushton |  | Metered via Tacoma
Tongue River |  | Out of Region
McCone Electric |  | Out of Region
Goldernwest Electric |  | Out of Region
Grand Electric |  | Out of Region
NOTE ON ADDITIONS
The following EIA-reported reatil sellers were added:
EIA Reporting Utility |  | Reason for Addition
Wells Rural Electric Co. |  | Served by BPA (but not reporting to EIA)
BPA non-EIA retail loads |  | Served by BPA (but in Nevada)
Lower Valley Energy |  | Served by BPA (but in ID and WY)
Note on A7: Charlie Grist: Utility list modified April 1, 2020 and April 9, 2020 Deleted 4 rows as out-of-region; Tongue River, McCone Electric, Goldenwest Electric, Grand Electric. Added a new row to separate out one industrial load customer of BPA that is no longer served by Bonneville. This also resulted in adjustment to the row for Bonneville which now includes other BPA direct sales to Port Townsend Paper, Navy bases, Fairchild AFB, DOE Richland, and Albany, OR. In addition BPA provided data on irrigation district loads whic were added into the BPA retail sales row. Power marketer sales were removed because they were duplicated in the OR and WA IOUs that serve those loads as "Delivery" sales. There were seven (7) of these in the 2018 EIA data. Identifired on sheet 2018 AMI & Substations. Behind-the-Meter sales were removed becasue thier energy is behind the meter and snot subject to distribution system losses. There were three (3) of these in the EIA data also identified in sheet 2018 AMI & Substations. Town of Rushton was removed becasue thier power is metered through Tacoma On the recommendation of BPA, Wells Rural Electric Co. was added to the list. Welss is a BPA cusstomer located in Nevada. Lower Valley Electic loads were updated to include WY portion which BPA serves The text box below this table describes the Bonneville analysis that these are based on.
Note on A15: Charlie Grist: Row 15 is not the same formulae as other cells. Row 15 is manually edited to reflect BPA reatil loads estimated from Tony Kock and Frank Brown (BPA) workbook that includes Irrigation Dist, SEATac, Military bases that are not in the EIA data. Several cells point to data on Tony's workbook
Note on A16: Charlie Grist: These data are manually enertered as correction to EIA data. One large customer (Alcoa) no longer BPA. Provided by BPA. See text box below.
Note on A141: Charlie Grist: Added April 9,2020 per BPA analysis
Note on C7: Charlie Grist: Column used to remove Power Marketers and Behind the Meter sales. PM sales are covered by utility Deliver-Only sales which are included in the table. Behind the Meter sales are not subject to CVR savings. If "Exclude" values show up, the row should be deleted.
Note on C15: Charlie Grist: Combination manual and EIA entry
Note on C16: Charlie Grist: Manual entry
Note on C141: Charlie Grist: Manual Entry
Note on E7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This field is used by Council staff for Plan scenarios that look at BPA and their public customers, only. Practically, this means all utilities except the six IOUs, and the three mid- C utilities; Grant, Chelan, Douglas. Reply: Also does not include any gen only utilities (avanvgrid, etc.)
Note on F7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: If HZ/CZ source data does not include a given utility, default to HZ 1 as it is most common in the region
Note on G7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: If HZ/CZ source data does not include a given utility, default to HZ 1 as it is most common in the region
Note on P7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Formula: Check to see if utility specific data is available. If not, use estimates from Input Data based on (Res+Comm) Sales.
Note on R7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Check to see if total number of feeders is known, and also check to see if % of total feeders that are urban is known. If total number of feeders isn't known, estimate by multiplying the Total Number of Distribution Substations by the typical number of feeders per substation for this size of utility. Then, if the % breakdown of urban vs. rural isn't known, use estimate from Input Data that would be typical to this size of utility.
Note on S7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: See comment for the Total Urban Feeders heading. Same process, but just checking the rural data
NOTE BONNEVILLE LOADS IN SYSTEM ANALYSIS SHEET. On the System Analysis tab, row 15 shows “BPA” with a retail load of 4,937,239 MWh/year. We were not sure what load this number represents. By exploring the direct service loads we discovered that it reflected the non-utility served loads, such at aluminum smelter Alcoa Ferndale, Port Townsend Paper, Navy bases, Fairchild AFB, DOE Richland, WA and Albany, OR. We confirmed with BPA Bulk Hub staff that BPA no longer serves the Alcoa load, which is still runing but served by others, at 3,400,000 MWh/yr. Therefore, this load was removed from the BPA load row 15 and a new row 16 was added to retain it as a regional load (all industrial). This has the effect of reducing the BPA portion of the potential.
Then additional BPA loads were added. These represent irrigation districts, Port of Seattle, Yakima Power, and others. A total of 968,893 MWh were added to the EIA reported BPA retail sales. This makes the total retail sales of BPA about 2,500,000 MWh. This includes about 1,500,000 reported to EIA and another 1,000,000 not reported to EIA but included here.

## 2018 AMI & Substation Data
2018 AMI & Substation Data
Source: Council Staff (MS) Analysis. Modifications: None Purpose: Feeder info: Careful! Much of this analysis was very manual. Do not copy formulas down as data sources were mixed and some rows have different formulae than others. AMI: Used to determine if utility has existing AMI infrastructure for use with CVR. Can use EIA 861 data for Advanced Mettering, but it was last collected in Jan 2017. For more recent info, google search was used on utility-by-utility basis. BPA Family: Manually creared field used for Council analyses consideriing just BPA and it's public customers. Practically, this means "yes" for all utilities except the six IOUs, and the three mid- C utilities; Grant, Chelan, Douglas, plus any generation only entities. Note that those generating only utilities have no sales eligible for DEI anyhow (since they own no distribution equipment) so this is mostly for completeness - functionally, yes or no doesnt change anything for them in this workbook. Substations: Using FERC Form 1 page 426 and 427 to total up. Transmission substations includes both attended (at plants) and unattended. If a substation was listed as being for both, it was included in just distrbution. | [10 empty] | AMI Analysis: Utilities in 2018 Sales sheet, listed in rank order of total MWh sales. Process was to look up AMI info for each utility as described in Purpose section, to the left. All utilities in green were checked and the "Has AMI' field was updated. This is not all utilities, yet, but accounts for 91.6% of total sales. Data source was primarily web searching on a utility by utility basis since EIA data had not been updated in quite a while. There is a possibility it may be in EIA-861 as the form guidance does mention it, but staff did not check to see if available there, yet.
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
Utility | Has AMI | Transmission Substations (n) | Distribution Substations (n) | Total Feeders | Urban/Suburban Feeders (%) | Rural Feeders (%) | Typical System Base Voltage | BPA Family? | Already doing LDC for CVR? | Owner Type | UTILITY_NAME | Total Sales (MWh) | Green utilities I have checked on, the rest are TBD
Alder Mutual Light Co, Inc | No | [6 empty] | Yes |  | Cooperative | Puget Sound Energy Inc | 22725923 | Total % Checked (on MWh basis) | 91.21%
Avangrid Renewables | No | [6 empty] | No |  | Power Marketer | PacifiCorp | 20852804
Avista Corp | Yes | 18 | 130 |  | 64% | 36% |  | No | Yes | Investor Owned | Portland General Electric Company | 19221496
Benton Rural Electric Assn | No | [6 empty] | Yes |  | Cooperative | Idaho Power Co | 14586522
Big Bend Electric Coop, Inc | No | [6 empty] | Yes |  | Cooperative | Seattle City of | 9074061
Blachly-Lane Cnty Coop El Assn | No | [6 empty] | Yes |  | Cooperative | Avista Corp | 8587540
Bonneville Power Administration | No | [6 empty] | Yes |  | Federal | Snohomish County PUD No 1 | 6481740
BP Energy Company | No | [6 empty] | No |  | Power Marketer | Bonneville Power Administration | 4937239
Calpine Energy Solutions, LLC | No | [6 empty] | No |  | Power Marketer | PUD No 2 of Grant County | 4910755
Canby Utility Board | No | [6 empty] | Yes |  | Municipal | PUD No 1 of Cowlitz County | 4839889
Central Electric Coop Inc | Yes | [6 empty] | Yes |  | Cooperative | Tacoma City of | 4617233
Central Lincoln People's Ut Dt | Yes | [6 empty] | Yes |  | Political Subdivision | PUD No 1 of Clark County | 4465033
City of Albion | No | [6 empty] | Yes |  | Municipal | NorthWestern Corporation | 3037016.4981
City of Ashland | No | [6 empty] | Yes |  | Municipal | Umatilla Electric Coop Assn | 2532517
City of Bandon | No | [6 empty] | Yes |  | Municipal | City of Eugene | 2341954
City of Blaine | No | [6 empty] | Yes |  | Municipal | PUD No 1 of Benton County | 1740849
City of Bonners Ferry | No | [6 empty] | Yes |  | Municipal | PUD No 1 of Chelan County | 1635017
City of Burley | No | [6 empty] | Yes |  | Municipal | Calpine Energy Solutions, LLC | 1482883
City of Cascade Locks | No | [6 empty] | Yes |  | Municipal | Flathead Electric Coop Inc | 1452386
City of Centralia | No | [6 empty] | Yes |  | Municipal | Shell Energy North America (US), L.P. | 1321863
City of Cheney | No | [6 empty] | Yes |  | Municipal | Central Lincoln People's Ut Dt | 1296364
City of Chewelah | No | [6 empty] | Yes |  | Municipal | Talen Energy Marketing, LLC | 1244657
City of Coulee Dam | No | [6 empty] | Yes |  | Municipal | PUD No 1 of Franklin County | 1042834
City of Declo | No | [6 empty] | Yes |  | Municipal | Clatskanie Peoples Util Dist | 1019901
City of Drain | No | [6 empty] | Yes |  | Municipal | PUD No 1 of Douglas County | 1005717
City of Ellensburg | No | [6 empty] | Yes |  | Municipal | PUD No 1 of Pend Oreille Cnty | 999951
City of Eugene | Yes | [6 empty] | Yes |  | Municipal | PUD No 1 of Grays Harbor Cnty | 956101
City of Forest Grove | No | [6 empty] | Yes |  | Municipal | City of Richland | 931884
City of Hermiston | No | [6 empty] | Yes |  | Municipal | PUD No 1 of Lewis County | 922377
City of Heyburn | No | [6 empty] | Yes |  | Municipal | Inland Power & Light Company | 915503
City of McCleary | No | [6 empty] | Yes |  | Municipal | BP Energy Company | 833304
City of Milton | No | [6 empty] | Yes |  | Municipal | Emerald People's Utility Dist | 790440
City of Milton-Freewater | No | [6 empty] | Yes |  | Municipal | Northern Wasco County PUD | 784410
City of Minidoka | No | [6 empty] | Yes |  | Municipal | City of Springfield | 765937
City of Monmouth | No | [6 empty] | Yes |  | Municipal | Central Electric Coop Inc | 721227
City of Plummer | No | [6 empty] | Yes |  | Municipal | McMinnville City of | 697188
City of Richland | No | [6 empty] | Yes |  | Municipal | Idaho Falls City of | 684813
City of Soda Springs | No | [6 empty] | Yes |  | Municipal | Oregon Trail El Cons Coop, Inc | 657478
City of Springfield | No | [6 empty] | Yes |  | Municipal | PUD No 3 of Mason County | 645683
City of Sumas | No | [6 empty] | Yes |  | Municipal | PUD No 1 of Clallam County | 632220
City of Troy | No | [6 empty] | Yes |  | Municipal | PUD No 1 of Okanogan County | 599394
City of Weiser | No | [6 empty] | Yes |  | Municipal | Peninsula Light Company | 581348
Clatskanie Peoples Util Dist | No | [6 empty] | Yes |  | Political Subdivision | Benton Rural Electric Assn | 545796
Clearwater Power Company | No | [6 empty] | Yes |  | Cooperative | Big Bend Electric Coop, Inc | 538117
Columbia Basin Elec Cooperative, Inc | No | [6 empty] | Yes |  | Cooperative | Columbia River Peoples Ut Dist | 482419
Columbia Power Coop Assn Inc | No | [6 empty] | Yes |  | Cooperative | Tenaska Power Services Co | 478403
Columbia River Peoples Ut Dist | No | [6 empty] | Yes |  | Political Subdivision | Tillamook Peoples Utility Dist | 469888
Columbia Rural Elec Assn, Inc | No | [6 empty] | Yes |  | Cooperative | Kootenai Electric Coop Inc | 464745
Constellation NewEnergy, Inc | No | [6 empty] | Yes |  | Power Marketer | Constellation NewEnergy, Inc | 408825
Consumers Power, Inc | No | [6 empty] | Yes |  | Cooperative | Midstate Electric Coop, Inc | 404275
Coos-Curry Electric Coop, Inc | No | [6 empty] | Yes |  | Cooperative | Consumers Power, Inc | 401942
Douglas Electric Coop, Inc | Yes | [6 empty] | Yes |  | Cooperative | Avangrid Renewables | 388321
East End Mutual Elec Co Ltd | No | [6 empty] | Yes |  | Cooperative | USBIA-Mission Valley Power | 380185
Elmhurst Mutual Power & Light Co | No | [6 empty] | Yes |  | Cooperative | PUD No 1 of Jefferson County | 376436
Emerald People's Utility Dist | Yes | [6 empty] | Yes |  | Political Subdivision | PUD No 1 of Klickitat County | 344507
Fall River Rural Elec Coop Inc | No | [6 empty] | Yes |  | Cooperative | Columbia Rural Elec Assn, Inc | 338669
Farmers Electric Company, Ltd | No | [6 empty] | Yes |  | Cooperative | Coos-Curry Electric Coop, Inc | 328481
Flathead Electric Coop Inc | Yes | [6 empty] | Yes |  | Cooperative | Salem Electric | 317746
Glacier Electric Coop, Inc | No | [6 empty] | Yes |  | Cooperative | Northern Lights, Inc | 307997
Goldenwest Electric Coop, Inc | No | [6 empty] | Yes |  | Cooperative | Fall River Rural Elec Coop Inc | 299875
Grand Electric Coop, Inc | No | [6 empty] | Yes |  | Cooperative | United Electric Co-op, Inc | 298313
Harney Electric Coop, Inc | No | [6 empty] | Yes |  | Cooperative | Pacific Public Utility District No 2 | 291438
Hood River Electric Coop | No | [6 empty] | Yes |  | Cooperative | Elmhurst Mutual Power & Light Co | 271244
Idaho Cnty L&P Coop Assn, Inc | No | [6 empty] | Yes |  | Cooperative | Port Angeles City of | 268893
Idaho Falls City of | Yes | [6 empty] | Yes |  | Municipal | City of Centralia | 260526
Idaho Power Co | Yes | 101 | 214 |  |  |  |  | No |  | Investor Owned | Lakeview Light & Power | 257169
Inland Power & Light Company | Yes | [6 empty] | Yes |  | Cooperative | City of Forest Grove | 246903
Kootenai Electric Coop Inc | No | [6 empty] | Yes |  | Cooperative | Lane Electric Coop Inc | 231436
Lakeview Light & Power | No | [6 empty] | Yes |  | Cooperative | Missoula Electric Coop, Inc | 229182
Lane Electric Coop Inc | No | [6 empty] | Yes |  | Cooperative | Modern Electric Water Company | 222686
Lincoln Electric Coop, Inc | No | [6 empty] | Yes |  | Cooperative | Vera Irrigation District #15 | 220910
Longroad Energy | No | [6 empty] | Yes |  | Behind the Meter | PUD No 1 of Whatcom County | 220310
Lost River Electric Coop Inc | No | [6 empty] | Yes |  | Cooperative | Raft River Rural Elec Coop Inc | 219252
Lower Valley Energy Inc | No | [6 empty] | Yes |  | Cooperative | Orcas Power & Light Coop | 208733
McCone Electric Coop Inc | No | [6 empty] | Yes |  | Cooperative | City of Ellensburg | 205282
McMinnville City of | No | [6 empty] | Yes |  | Municipal | Clearwater Power Company | 189153
Midstate Electric Coop, Inc | No | [6 empty] | Yes |  | Cooperative | Canby Utility Board | 185047
Missoula Electric Coop, Inc | No | [6 empty] | Yes |  | Cooperative | City of Ashland | 171916
Modern Electric Water Company | No | [6 empty] | Yes |  | Cooperative | Blachly-Lane Cnty Coop El Assn | 171676
Nespelem Valley Elec Coop, Inc | No | [6 empty] | Yes |  | Cooperative | Glacier Electric Coop, Inc | 170470
Northern Lights, Inc | No | [6 empty] | Yes |  | Cooperative | Vigilante Electric Coop, Inc | 166498
Northern Wasco County PUD | Yes | [6 empty] | Yes |  | Political Subdivision | Ravalli County Elec Coop, Inc | 154006
NorthWestern Corporation | No | [6 empty] | No |  | Investor Owned | Douglas Electric Coop, Inc | 151034
Ohop Mutual Light Company, Inc | No | [6 empty] | Yes |  | Cooperative | City of Cheney | 139677
Okanogan County Elec Coop, Inc | Yes | [6 empty] | Yes |  | Cooperative | WAPA-- Western Area Power Administration | 122801
Orcas Power & Light Coop | No | [6 empty] | Yes |  | Cooperative | PUD No 1 of Skamania Co | 120564
Oregon Trail El Cons Coop, Inc | Yes | [6 empty] | Yes |  | Cooperative | Hood River Electric Coop | 118389
Pacific Public Utility District No 2 | No | [6 empty] | Yes |  | Political Subdivision | Lincoln Electric Coop, Inc | 117955
PacifiCorp | Yes | 57 | 291 |  |  |  |  | No | Yes | Investor Owned | City of Burley | 115765
Parkland Light & Water Company | No | [6 empty] | Yes |  | Cooperative | Parkland Light & Water Company | 113395
Peninsula Light Company | Yes | [6 empty] | Yes |  | Cooperative | Columbia Basin Elec Cooperative, Inc | 108960
Port Angeles City of | No | [6 empty] | Yes |  | Municipal | City of Hermiston | 107121
Portland General Electric Company | Yes | 56 | 164 |  |  |  |  | No | Yes | Investor Owned | Wasco Electric Coop, Inc | 106704
PUD No 1 of Asotin County | No | [6 empty] | Yes |  | Municipal | City of Milton-Freewater | 103892
PUD No 1 of Benton County | Yes | [6 empty] | Yes |  | Political Subdivision | Harney Electric Coop, Inc | 101545
PUD No 1 of Chelan County | No | [6 empty] | No |  | Political Subdivision | Tongue River Electric Coop Inc | 99260
PUD No 1 of Clallam County | Yes | [6 empty] | Yes |  | Political Subdivision | Salmon River Electric Coop Inc | 98091
PUD No 1 of Clark County | No | [6 empty] | Yes |  | Political Subdivision | PUD No 1 of Kittitas County | 97901
PUD No 1 of Cowlitz County | Yes | [6 empty] | Yes |  | Political Subdivision | Tanner Electric Coop | 90680
PUD No 1 of Douglas County | No | [6 empty] | No |  | Political Subdivision | Ohop Mutual Light Company, Inc | 82179
PUD No 1 of Ferry County | No | [6 empty] | Yes |  | Political Subdivision | Rupert City of | 77418
PUD No 1 of Franklin County | No | [6 empty] | Yes |  | Political Subdivision | City of Bonners Ferry | 77390
PUD No 1 of Grays Harbor Cnty | Yes | [6 empty] | Yes |  | Political Subdivision | City of Blaine | 76758
PUD No 1 of Jefferson County | No | [6 empty] | Yes |  | Political Subdivision | PUD No 1 of Mason County | 75659
PUD No 1 of Kittitas County | No | [6 empty] | Yes |  | Political Subdivision | McCone Electric Coop Inc | 75226
PUD No 1 of Klickitat County | No | [6 empty] | Yes |  | Political Subdivision | Lost River Electric Coop Inc | 73841
PUD No 1 of Lewis County | No | [6 empty] | Yes |  | Political Subdivision | City of Monmouth | 71954
PUD No 1 of Mason County | No | [6 empty] | Yes |  | Political Subdivision | Lower Valley Energy Inc | 71601
PUD No 1 of Okanogan County | No | [6 empty] | Yes |  | Political Subdivision | PUD No 1 of Ferry County | 66726
PUD No 1 of Pend Oreille Cnty | No | [6 empty] | Yes |  | Political Subdivision | West Oregon Electric Coop Inc | 64678
PUD No 1 of Skamania Co | No | [6 empty] | Yes |  | Political Subdivision | City of Heyburn | 62071
PUD No 1 of Wahkiakum County | No | [6 empty] | Yes |  | Political Subdivision | Nespelem Valley Elec Coop, Inc | 60886
PUD No 1 of Whatcom County | No | [6 empty] | Yes |  | Political Subdivision | City of Bandon | 60353
PUD No 2 of Grant County | Yes | [6 empty] | No |  | Political Subdivision | South Side Electric, Inc | 58794
PUD No 3 of Mason County | No | [6 empty] | Yes |  | Political Subdivision | Okanogan County Elec Coop, Inc | 58020
Puget Sound Energy Inc | Yes | 25 | 349 |  |  |  |  | No |  | Investor Owned | Idaho Cnty L&P Coop Assn, Inc | 51784
Raft River Rural Elec Coop Inc | No | [6 empty] | Yes |  | Cooperative | City of Weiser | 48289
Ravalli County Elec Coop, Inc | No | [6 empty] | Yes |  | Cooperative | PUD No 1 of Wahkiakum County | 41044
Riverside Electric Cooperative | No | [6 empty] | Yes |  | Cooperative | Surprise Valley Electrification Corp. | 37041
Rupert City of | No | [6 empty] | Yes |  | Municipal | Town of Steilacoom | 37015
Salem Electric | No | [6 empty] | Yes |  | Cooperative | City of Plummer | 33046
Salmon River Electric Coop Inc | No | [6 empty] | Yes |  | Cooperative | City of Milton | 33000
Seattle City of | Yes | [6 empty] | Yes |  | Municipal | City of Sumas | 32871
Shell Energy North America (US), L.P. | No | [6 empty] | Yes |  | Power Marketer | City of McCleary | 31802
Snohomish County PUD No 1 | No | [6 empty] | Yes | Yes | Political Subdivision | SolarCity Corporation | 31484
SolarCity Corporation | No | [6 empty] | Yes |  | Behind the Meter | Town of Eatonville | 26769
South Side Electric, Inc | No | [6 empty] | Yes |  | Cooperative | City of Soda Springs | 26496
Surprise Valley Electrification Corp. | No | [6 empty] | Yes |  | Cooperative | East End Mutual Elec Co Ltd | 24404
Tacoma City of | Yes | [6 empty] | Yes |  | Municipal | Goldenwest Electric Coop, Inc | 24212
Talen Energy Marketing, LLC | No | [6 empty] | Yes |  | Power Marketer | Columbia Power Coop Assn Inc | 23378
Tanner Electric Coop | No | [6 empty] | Yes |  | Cooperative | City of Cascade Locks | 22149
Tenaska Power Services Co | No | [6 empty] | Yes |  | Power Marketer | City of Chewelah | 21475
Tillamook Peoples Utility Dist | No | [6 empty] | Yes |  | Political Subdivision | Riverside Electric Cooperative | 21311
Tongue River Electric Coop Inc | No | [6 empty] | Yes |  | Cooperative | City of Coulee Dam | 16437
Town of Eatonville | No | [6 empty] | Yes |  | Municipal | City of Troy | 16371
Town of Ruston | No | [6 empty] | Yes |  | Municipal | City of Drain | 15996
Town of Steilacoom | No | [6 empty] | Yes |  | Municipal | Town of Ruston | 7475
Umatilla Electric Coop Assn | Yes | [6 empty] | Yes |  | Cooperative | Alder Mutual Light Co, Inc | 5101
United Electric Co-op, Inc | No | [6 empty] | Yes |  | Cooperative | Farmers Electric Company, Ltd | 3803
USBIA-Mission Valley Power | No | [6 empty] | Yes |  | Federal | City of Albion | 2918
Vera Irrigation District #15 | No | [6 empty] | Yes |  | Political Subdivision | Longroad Energy | 1502
Vigilante Electric Coop, Inc | No | [6 empty] | Yes |  | Cooperative | City of Minidoka | 811
WAPA-- Western Area Power Administration | No | [6 empty] | Yes |  | Federal | City of Declo | 273
Wasco Electric Coop, Inc | No | [6 empty] | Yes |  | Cooperative | PUD No 1 of Asotin County | 247
Wells Rural Electric Co. | Yes | [6 empty] | Yes |  | 0 | Wells Rural Electric Co. | 756803
West Oregon Electric Coop Inc | No | [6 empty] | Yes |  | Cooperative | Grand Electric Coop, Inc | 128
Note on B11: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: No based on entity type
Note on B12: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: No based on entity type
Note on B13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: No based on entity type
Note on B31: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Currently installing them, expected to be done in 2021.
Note on B41: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Issued an RFP in 2018 but doesn't look like they've moved since
Note on B62: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Done as part of BPA smart grid
Note on B87: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: For MT. Could become yes after HB 267 from 2019, but TBD for now.
Note on B100: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Theyve been looking at it but not moving forward as of 2019
Note on B101: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: https://www.clallampud.net/advanced-meter-information/
Note on B103: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: In place now and current RFP for upgrade as of 2019
Note on B106: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Looks like they are relacing them as they age out
Note on B107: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Couldn't find info from Gray's but coverage from Jeff PUD in WA said that Gray's had it https://www.peninsuladailynews.com/news/jefferson-county-pud-puts-smart-meters-on-hold/
Note on B128: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: No based on entity type
Note on B133: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: They are currently installing them, should be up and going in 2022
Note on B134: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: No based on entity type
Note on C93: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: OR WA ID MT FERC Form 1
Note on D93: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: OR WA ID MT
Note on E120: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: See PGE 2013 Smartgrid report for total list and urban/rural breakdown
Note on F7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Per table 3 of Avista's 2018 Reliability Reort
Note on F120: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: See PGE 2013 Smartgrid report for total list and urban/rural breakdown
Note on G120: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: See PGE 2013 Smartgrid report for total list and urban/rural breakdown
Note on J4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Some utilities may already be doing LDC for CVR and therefore they would not be eligible for ECM1. It is important to note that utilities could also be doing LDC not for the goal of lowering voltages, but simply to stay in range on both high and low side. So "doing LDC" alone is not enough information.

## HeatingCooling Zone
Heating & Cooling Zone Data |  |  |  |  | Electric Heating By Heating Zone
Source: RTF_ClimateZoneCalculate_v2_0.xlsm Modifications: Manually cross-walked the utility name from the RTF workbook to the Utility Name used in this work (from EIA data) to allow VLOOKUP to work in Analysis sheet. Purpose: This data was used to help determine how the CVRf Effectiveness should change based on the HZ/CZ of a given utility. |  |  |  |  | Source: RBSA_II_HVAC_saturation_02OCT2019.xlsx Modifications: None Purpose: This data was used to help determine how the CVRf Effectiveness should change based on the HZ/CZ of a given utility. Thermostatic loads are not very senstive to CVR, so areas with a large share of electric heating should see lower overall CVR factors. The field "Percent of homes that are program-eligible" refers to the share of home sin HZ with electric heating of some kind, and then the table "Main electric heat source" describes the breakdown for those customers who are electric heating. The data here is informational and was used for making an informed and literature backed (but not directly quantiative decision) about how to reduce CVR effectiveness through the CVRf field based on heating zones.
1 | 2 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 3 | 4 | 1 | 2
Utility (Used in this work) | Utility (From RTF) | State | Heating Zone - TMY3, Daily | Cooling Zone - TMY3, Daily | Source: RBSA_II_HVAC_saturation_02OCT2019.xlsx Modifications: None Purpose: This data was used to help determine how the CVRf Effectiveness should change based on the HZ/CZ of a given utility. Thermostatic loads are not very senstive to CVR, so areas with a large share of electric heating should see lower overall CVR factors. The field "Percent of homes that are program-eligible" refers to the share of home sin HZ with electric heating of some kind, and then the table "Main electric heat source" describes the breakdown for those customers who are electric heating. The data here is informational and was used for making an informed and literature backed (but not directly quantiative decision) about how to reduce CVR effectiveness through the CVRf field based on heating zones. 9: Equipment share estimates by Zone; Source: RBSA_II_HVAC_saturation_02OCT2019.xlsx Modifications: None Purpose: This data was used to help determine how the CVRf Effectiveness should change based on the HZ/CZ of a given utility. Thermostatic loads are not very senstive to CVR, so areas with a large share of electric heating should see lower overall CVR factors. The field "Percent of homes that are program-eligible" refers to the share of home sin HZ with electric heating of some kind, and then the table "Main electric heat source" describes the breakdown for those customers who are electric heating. The data here is informational and was used for making an informed and literature backed (but not directly quantiative decision) about how to reduce CVR effectiveness through the CVRf field based on heating zones. 10: Main electric heat source
Alder Mutual Light Co, Inc | Alder Mutual Light Company | WA | 1 | 1 | Program eligibility | Total number of homes | Total number of weatherization-program-eligible homes | "p" Percent of homes that are program-eligible | Sample Size | Standard error of p | Relative precision (90% confidence) |  |  | elec ashp | elec minisplit | elec furnace | elec baseboard | elec zonal (other)
PUD No 1 of Asotin County | Asotin County PUD | WA | 1 | 3 | HZ 1 | 3419318.5948 | 1523180.9996 | 44.55% | 759 | 1.804% | 6.662% |  | HZ 1 | 40.11% | 9.275% | 9.122% | 18.23% | 23.27%
Avista Corp | Avista Corporation | ID | 2 | 2 | HZ 2 | 720178.2297 | 281222.0876 | 39.05% | 237 | 3.169% | 13.35% |  | HZ 2 | 35.67% | 8.763% | 5.799% | 28.59% | 21.17%
Avista Corp | Avista Corporation | WA | 2 | 2 | HZ 3 | 299505.1755 | 105967.5701 | 35.38% | 104 | 4.689% | 21.8% |  | HZ 3 | 18.65% | 6.025% | 18.9% | 36.78% | 19.64%
| BEARTOOTH ELECTRIC COOP, INC | MT | 2 | 2 | HZ 2/3 | 1019683.4052 | 387189.6577 | 37.97% | 341 | 2.628% | 11.39% |  | HZ 2/3 | 30.86% | 7.99% | 9.502% | 30.9% | 20.74%
Benton Rural Electric Assn | Benton Rural Electric Association | WA | 1 | 3 | HZ 1/2/3 | 4439002 | 1910370.6573 | 43.04% | 1100 | 1.493% | 5.706% |  | HZ 1/2/3 | 38.25% | 9.017% | 9.198% | 20.77% | 22.76%
Big Bend Electric Coop, Inc | Big Bend Electric Cooperative | WA | 1 | 3
| BIG FLAT ELECTRIC COOP INC | MT | 3 | 3
| Big Horn County Electric Cooperative | MT | 2 | 2
Blachly-Lane Cnty Coop El Assn | Blachly-Lane Electric Cooperative | OR | 1 | 2
Canby Utility Board | Canby Utility Board | OR | 1 | 2
Central Electric Coop Inc | Central Electric Cooperative, Inc. | OR | 2 | 1
Central Lincoln People's Ut Dt | Central Lincoln People's Utility District | OR | 1 | 1
City of Albion | City of Albion | ID | 2 | 3
City of Ashland | City of Ashland | OR | 1 | 3
City of Bandon | City of Bandon | OR | 1 | 1
City of Blaine | City of Blaine | WA | 1 | 1
City of Bonners Ferry | City of Bonners Ferry | ID | 2 | 2
City of Burley | City of Burley | ID | 2 | 3
City of Cascade Locks | City of Cascade Locks | OR | 1 | 2
| CITY OF CASHMERE | WA | 1 | 3
City of Centralia | CITY OF CENTRALIA | WA | 1 | 1
City of Cheney | City of Cheney | WA | 2 | 2
City of Chewelah | City of Chewelah | WA | 2 | 2
City of Declo | City of Declo | ID | 2 | 3
City of Drain | City of Drain | OR | 1 | 1
City of Ellensburg | City of Ellensburg | WA | 2 | 2
City of Forest Grove | City of Forest Grove | OR | 1 | 1
City of Heyburn | City of Heyburn | ID | 2 | 3
Idaho Falls City of | City of Idaho Falls | ID | 3 | 1
City of McCleary | City of McCleary | WA | 1 | 1
City of Milton | City of Milton | WA | 1 | 1
City of Milton-Freewater | City of Milton-Freewater | OR | 1 | 3
City of Minidoka | City of Minidoka | ID | 2 | 3
City of Monmouth | City of Monmouth | OR | 1 | 1
City of Plummer | City of Plummer | ID | 2 | 2
Port Angeles City of | City of Port Angeles | WA | 1 | 1
City of Richland | City of Richland, Washington | WA | 1 | 3
Rupert City of | City of Rupert | ID | 2 | 3
Seattle City of | City of Seattle, City Light Dept | WA | 1 | 1
City of Soda Springs | City of Soda Springs | ID | 3 | 1
City of Sumas | City of Sumas | WA | 1 | 1
City of Troy | City of Troy | MT | 2 | 2
City of Weiser | City of Weiser | ID | 1 | 3
PUD No 1 of Clark County | Clark Public Utilities | WA | 1 | 2
Clatskanie Peoples Util Dist | Clatskanie People's Utility District | OR | 1 | 1
Clearwater Power Company | Clearwater Power Company | ID | 1 | 3
Clearwater Power Company | Clearwater Power Company | WA | 1 | 3
Columbia Basin Elec Cooperative, Inc | Columbia Basin Electric Cooperative, Inc. | OR | 1 | 3
Columbia Power Coop Assn Inc | Columbia Power Cooperative Association | OR | 1 | 3
Columbia River Peoples Ut Dist | Columbia River People's Utility District | OR | 1 | 1
Columbia Rural Elec Assn, Inc | Columbia Rural Electric Association | OR | 1 | 3
Columbia Rural Elec Assn, Inc | Columbia Rural Electric Association | WA | 1 | 3
Consumers Power, Inc | Consumers Power, Inc. | OR | 1 | 2
Coos-Curry Electric Coop, Inc | Coos-Curry Electric Cooperative, Inc. | OR | 1 | 1
Douglas Electric Coop, Inc | Douglas Electric Cooperative, Inc. | OR | 1 | 2
East End Mutual Elec Co Ltd | East End Mutual Electric Company, LTD | ID | 2 | 3
Elmhurst Mutual Power & Light Co | Elmhurst Mutual Power & Light Company | WA | 1 | 1
Emerald People's Utility Dist | Emerald PUD | OR | 1 | 1
| Eugene Water & Electric Board | OR | 1 | 1
Fall River Rural Elec Coop Inc | Fall River Rural Electric Cooperative, Inc. | ID | 3 | 1
Fall River Rural Elec Coop Inc | Fall River Rural Electric Cooperative, Inc. | MT | 3 | 3
Farmers Electric Company, Ltd | Farmer's Electric Company | ID | 2 | 3
| FERGUS ELECTRIC COOP, INC | MT | 3 | 3
Flathead Electric Coop Inc | Flathead Electric Cooperative, Inc. | MT | 3 | 3
Glacier Electric Coop, Inc | Glacier Electric Cooperative, Inc. | MT | 3 | 3
Goldenwest Electric Coop, Inc | GOLDENWEST ELECTRIC COOP, INC | MT | 3 | 3
Harney Electric Coop, Inc | Harney Electric Cooperative, Inc. | OR | 2 | 1
| Hermiston Energy Services | OR | 1 | 2
| HILL COUNTY ELECTRIC COOP, INC | MT | 3 | 3
Hood River Electric Coop | Hood River Electric Cooperative | OR | 1 | 3
Idaho Cnty L&P Coop Assn, Inc | Idaho County Light & Power Cooperative Association | ID | 1 | 3
Idaho Power Co | Idaho Power Company | ID | 1 | 3
Idaho Power Co | Idaho Power Company | OR | 1 | 3
Inland Power & Light Company | Inland Power & Light Company | ID | 2 | 2
Inland Power & Light Company | Inland Power & Light Company | WA | 2 | 2
Kootenai Electric Coop Inc | Kootenai Electric Cooperative, Inc. | ID | 2 | 2
Lakeview Light & Power | Lakeview Light & Power Company | WA | 1 | 1
Lane Electric Coop Inc | Lane Electric Cooperative, Inc. | OR | 1 | 1
Lincoln Electric Coop, Inc | Lincoln Electric Cooperative, Inc. | MT | 3 | 3
Lost River Electric Coop Inc | Lost River Electric Cooperative, Inc. | ID | 2 | 3
Lower Valley Energy Inc | Lower Valley Energy, Inc. | WY | 3 | 1
| LOWER YELLOWSTONE R E A, INC | MT | 3 | 3
| MARIAS RIVER ELECTRIC COOP INC | MT | 3 | 3
McCone Electric Coop Inc | MCCONE ELECTRIC COOP INC | MT | 3 | 3
| MDU RESOURCES GROUP INC | MT | 3 | 3
Midstate Electric Coop, Inc | Midstate Electric Cooperative, Inc. | OR | 2 | 1
| MID-YELLOWSTONE ELEC COOP, INC | MT | 3 | 2
USBIA-Mission Valley Power | Mission Valley Power | MT | 3 | 2
Missoula Electric Coop, Inc | Missoula Electric Cooperative, Inc. | MT | 2 | 3
Modern Electric Water Company | Modern Electric Water Company | WA | 2 | 2
Nespelem Valley Elec Coop, Inc | Nespelem Valley Electric Cooperative, Inc. | WA | 1 | 3
| NORTHERN ELECTRIC COOP, INC | MT | 3 | 3
Northern Lights, Inc | Northern Lights, Inc. | ID | 2 | 2
Northern Lights, Inc | Northern Lights, Inc. | MT | 2 | 2
Northern Wasco County PUD | Northern Wasco County People's Utility District | OR | 1 | 3
NorthWestern Corporation | NorthWestern Energy, LLC | MT | 3 | 3
Ohop Mutual Light Company, Inc | Ohop Mutual Light Company | WA | 1 | 1
Okanogan County Elec Coop, Inc | Okanogan County Electric Cooperative, Inc. | WA | 1 | 3
PUD No 1 of Okanogan County | Okanogan County Public Utility District No. 1 | WA | 1 | 3
Orcas Power & Light Coop | Orcas Power & Light Cooperative | WA | 1 | 1
Oregon Trail El Cons Coop, Inc | Oregon Trail Electric Consumers Cooperative, Inc. | OR | 2 | 1
| Pacificorp (ID) | ID | 3 | 1
PacifiCorp | Pacificorp (OR) | OR | 1 | 2
| Pacificorp (WA) | WA | 1 | 2
| PARK ELECTRIC COOP INC | MT | 3 | 3
Parkland Light & Water Company | Parkland Light and Water Co. | WA | 1 | 1
PUD No 1 of Pend Oreille Cnty | Pend Oreille County PUD No. 1 | WA | 2 | 2
Peninsula Light Company | Peninsula Light Company | WA | 1 | 1
Portland General Electric Company | Portland General Electric Company | OR | 1 | 2
PUD No 1 of Skamania Co | Public Utility District #1 of Skamania County | WA | 1 | 2
PUD No 1 of Chelan County | Public Utility District No. 1 of Chelan County | WA | 1 | 3
PUD No 1 of Clallam County | Public Utility District No. 1 of Clallam County | WA | 1 | 1
PUD No 1 of Cowlitz County | Public Utility District No. 1 of Cowlitz County | WA | 1 | 1
PUD No 1 of Douglas County | Public Utility District No. 1 of Douglas County | WA | 1 | 3
PUD No 1 of Ferry County | Public Utility District No. 1 of Ferry County | WA | 2 | 2
PUD No 1 of Franklin County | Public Utility District No. 1 of Franklin County | WA | 1 | 3
PUD No 1 of Grays Harbor Cnty | Public Utility District No. 1 of Grays Harbor County | WA | 1 | 1
PUD No 1 of Jefferson County | Public Utility District No. 1 of Jefferson County | WA | 1 | 1
PUD No 1 of Kittitas County | Public Utility District No. 1 of Kittitas County | WA | 3 | 1
PUD No 1 of Klickitat County | Public Utility District No. 1 of Klickitat County | WA | 1 | 3
PUD No 1 of Lewis County | Public Utility District No. 1 of Lewis County | WA | 1 | 1
PUD No 1 of Mason County | Public Utility District No. 1 of Mason County | WA | 1 | 1
Snohomish County PUD No 1 | Public Utility District No. 1 Of Snohomish County | WA | 1 | 1
PUD No 1 of Wahkiakum County | Public Utility District No. 1 of Wahkiakum County | WA | 1 | 1
PUD No 2 of Grant County | Public Utility District No. 2 of Grant County, Was | WA | 1 | 3
Pacific Public Utility District No 2 | Public Utility District No. 2 of Pacific County | WA | 1 | 1
PUD No 3 of Mason County | Public Utility District No. 3 of Mason County | WA | 1 | 1
PUD No 1 of Benton County | PUD NO 1 OF BENTON COUNTY | WA | 1 | 3
Puget Sound Energy Inc | Puget Sound Energy, Inc. | WA | 1 | 1
Raft River Rural Elec Coop Inc | Raft River Rural Electric Cooperative, Inc. | ID | 2 | 3
Ravalli County Elec Coop, Inc | Ravalli County Electric Cooperative, Inc. | MT | 2 | 3
Riverside Electric Cooperative | Riverside Electric Company, LTD | ID | 2 | 3
Town of Ruston | Ruston | WA | 1 | 1
Salem Electric | Salem Electric | OR | 1 | 1
Salmon River Electric Coop Inc | Salmon River Electric Cooperative, Inc. | ID | 2 | 2
| SHERIDAN ELECTRIC COOP, INC | MT | 3 | 3
| SOUTHEAST ELECTRIC COOP, INC | MT | 3 | 3
| Springfield Utility Board | OR | 1 | 1
| SUN RIVER ELECTRIC COOP, INC | MT | 3 | 3
Surprise Valley Electrification Corp. | Surprise Valley Electrification Corporation | CA | 2 | 2
Tacoma City of | Tacoma Power | WA | 1 | 1
Tanner Electric Coop | Tanner Electric Cooperative | WA | 1 | 1
McMinnville City of | The City of McMinnville | OR | 1 | 2
Tillamook Peoples Utility Dist | Tillamook People's Utility District | OR | 1 | 1
Tongue River Electric Coop Inc | TONGUE RIVER ELECTRIC COOP INC | MT | 3 | 3
Town of Eatonville | Town of Eatonville | WA | 1 | 1
Town of Steilacoom | Town of Steilacoom | WA | 1 | 1
Umatilla Electric Coop Assn | Umatilla Electric Cooperative | OR | 1 | 3
| Umpqua Indian Utility Cooperative | OR | 1 | 2
United Electric Co-op, Inc | United Electric Co-op, Inc. | ID | 2 | 3
| VALLEY ELECTRIC COOP, INC | MT | 3 | 3
Vera Irrigation District #15 | Vera Water & Power | WA | 2 | 2
Vigilante Electric Coop, Inc | Vigilante Electric Cooperative, Inc. | MT | 3 | 3
Wasco Electric Coop, Inc | Wasco Electric Cooperative, Inc. | OR | 1 | 3
| Wells Rural Electric Co. | NV | 2 | 1
West Oregon Electric Coop Inc | West Oregon Electric Cooperative, Inc. | OR | 1 | 1
| Yakama Power | WA | 2 | 2
| YELLOWSTONE VALLEY ELEC CO-OP | MT | 2 | 2

## 2018 Sales
2018 Regional Sales Numbers
Source: "2018 Sales Source Data" Sheet Modifications: None Purpose: Aggregate data from utilities with multile rows in the original source data. For more info, see source sheet.
1 | 2 | 3 | 4 | 5 | 6 | 7
Data
UTILITY_NAME | Sum of Res Sales (MWh) | Sum of Com Sales (MWh) | Sum of Ind Sales (MWh) | Sum of Trans Sales (MWh) | Sum of Total Sales (MWh) | Sum of Total Consumers (n)
Alder Mutual Light Co, Inc | 4628.0985 | 472.9015 | 0 | 0 | 5101 | 292
Avangrid Renewables |  | 388321 |  |  | 388321 | 3
Avista Corp | 3626871 | 3188388 | 1772281 | 0 | 8587540 | 387662
Benton Rural Electric Assn | 208105 | 130729 | 206962 |  | 545796 | 14424
Big Bend Electric Coop, Inc | 103377 | 106379 | 328361 | 0 | 538117 | 9349
Blachly-Lane Cnty Coop El Assn | 49387 | 10817 | 111472 |  | 171676 | 3616
Bonneville Power Administration | 0 | 782505 | 4154734 | 0 | 4937239 | 11
BP Energy Company | 0 | 0 | 833304 | 0 | 833304 | 2
Calpine Energy Solutions, LLC | 0 | 1202213 | 280670 | 0 | 1482883 | 40
Canby Utility Board | 76959 | 72556 | 35532 | 0 | 185047 | 7462
Central Electric Coop Inc | 491376 | 121002 | 108849 |  | 721227 | 34508
Central Lincoln People's Ut Dt | 415852 | 191006 | 689506 |  | 1296364 | 39181
City of Albion | 2011.3514 | 906.6486 | 0 | 0 | 2918 | 214
City of Ashland | 86287 | 85629 |  |  | 171916 | 11978
City of Bandon | 34708 | 24096 | 1549 | 0 | 60353 | 3777
City of Blaine | 26502 | 38836 | 11420 |  | 76758 | 3395
City of Bonners Ferry | 26446.0485 | 27999.376 | 22944.5755 | 0 | 77390 | 2767
City of Burley | 46306 | 69459 |  |  | 115765 | 4768
City of Cascade Locks | 10091.8732 | 12057.1268 | 0 | 0 | 22149 | 911
City of Centralia | 115021 | 33489 | 112016 |  | 260526 | 10282
City of Cheney | 57860 | 67246 | 14571 | 0 | 139677 | 5676
City of Chewelah | 11436.6981 | 10396.9983 | 0 | 0 | 21475 | 1293
City of Coulee Dam | 9334.616 | 7102.384 | 0 | 0 | 16437 | 597
City of Declo | 144.1277 | 87.3053 | 32.1599 | 0 | 273 | 130
City of Drain | 7592.5452 | 3513.3088 | 4890.146 | 0 | 15996 | 753
City of Ellensburg | 76934 | 120212 | 8136 |  | 205282 | 9774
City of Eugene | 914487 | 869518 | 557949 | 0 | 2341954 | 93962
City of Forest Grove | 112058 | 24199 | 110646 |  | 246903 | 10126
City of Hermiston | 51860 | 55261 |  |  | 107121 | 5366
City of Heyburn | 30693.6774 | 10571.2641 | 20806.0585 | 0 | 62071 | 1664
City of McCleary | 16771.8821 | 4615.2841 | 10414.8338 | 0 | 31802 | 1119
City of Milton | 23109.7535 | 9890.2465 | 0 | 0 | 33000 | 3512
City of Milton-Freewater | 58599 | 14301 | 30992 |  | 103892 | 4408
City of Minidoka | 773.473 | 37.527 | 0 | 0 | 811 | 45
City of Monmouth | 44181 | 27773 |  |  | 71954 | 4596
City of Plummer | 10182.5212 | 8809.5158 | 14053.963 | 0 | 33046 | 963
City of Richland | 338631 | 435831 | 157422 |  | 931884 | 24527
City of Soda Springs | 11797.9554 | 13965.6271 | 397.5642 | 0 | 26496 | 1871
City of Springfield | 370238 | 256249 | 139450 |  | 765937 | 32276
City of Sumas | 6144.1537 | 5377.8004 | 21349.0459 | 0 | 32871 | 900
City of Troy | 11318.4437 | 4989.2931 | 63.2632 | 0 | 16371 | 978
City of Weiser | 24693.4239 | 13947.9396 | 9647.6365 | 0 | 48289 | 3482
Clatskanie Peoples Util Dist | 72896 | 17193 | 929812 | 0 | 1019901 | 4201
Clearwater Power Company | 129142 | 30522 | 29489 | 0 | 189153 | 10754
Columbia Basin Elec Cooperative, Inc | 39961 | 27108 | 41891 |  | 108960 | 3890
Columbia Power Coop Assn Inc | 13579 | 4549 | 5250 |  | 23378 | 1894
Columbia River Peoples Ut Dist | 215305 | 102200 | 164914 | 0 | 482419 | 19443
Columbia Rural Elec Assn, Inc | 53126 | 72355 | 213188 |  | 338669 | 5978
Constellation NewEnergy, Inc | 0 | 188845 | 219980 | 0 | 408825 | 111
Consumers Power, Inc | 273091 | 87933 | 40918 |  | 401942 | 22655
Coos-Curry Electric Coop, Inc | 179106 | 91608 | 57767 |  | 328481 | 17878
Douglas Electric Coop, Inc | 125093 | 18752 | 7189 |  | 151034 | 10087
East End Mutual Elec Co Ltd | 15232.1858 | 9171.8142 | 0 | 0 | 24404 | 747
Elmhurst Mutual Power & Light Co | 229819 | 41425 |  |  | 271244 | 15462
Emerald People's Utility Dist | 285445 | 108536 | 396459 |  | 790440 | 21573
Fall River Rural Elec Coop Inc | 172199 | 127676 |  |  | 299875 | 16659
Farmers Electric Company, Ltd | 1801.7107 | 1827.7997 | 0 | 0 | 3803 | 125
Flathead Electric Coop Inc | 754053 | 457949 | 240384 |  | 1452386 | 66911
Glacier Electric Coop, Inc | 70883 | 79672 | 19915 | 0 | 170470 | 7728
Goldenwest Electric Coop, Inc |  |  |  |  | 24212 | 805
Grand Electric Coop, Inc | 128 |  |  |  | 128 | 14
Harney Electric Coop, Inc | 30166 |  | 187431 |  | 217597 | 3682
Hood River Electric Coop | 52252 | 6434 | 59703 |  | 118389 | 3865
Idaho Cnty L&P Coop Assn, Inc | 42956.7001 | 8617.3969 | 209.903 | 0 | 51784 | 4003
Idaho Falls City of | 282284 | 334872 | 67657 | 0 | 684813 | 28175
Idaho Power Co | 5134576 | 4104941 | 5347005 | 0 | 14586522 | 551455
Inland Power & Light Company | 656947 | 167846 | 90710 |  | 915503 | 41707
Kootenai Electric Coop Inc | 321923 | 112601 | 30221 | 0 | 464745 | 25548
Lakeview Light & Power | 106703 | 89895 | 60571 |  | 257169 | 10097
Lane Electric Coop Inc | 185955 | 41125 | 4356 |  | 231436 | 12850
Lincoln Electric Coop, Inc | 81687 | 29465 | 6803 |  | 117955 | 5887
Longroad Energy |  | 1502 |  |  | 1502 | 24
Lost River Electric Coop Inc | 27149.6098 | 5660.9651 | 0 | 0 | 73841 | 2728
Lower Valley Energy Inc | 463238 | 250390 | 80023 |  | 793651 | 28129
McCone Electric Coop Inc | 51060 | 22501 | 1665 | 0 | 75226 | 5289
McMinnville City of | 190078 | 174545 | 332565 | 0 | 697188 | 16416
Midstate Electric Coop, Inc | 258677 | 117183 | 28415 | 0 | 404275 | 19362
Missoula Electric Coop, Inc | 164982 | 46587 | 17613 |  | 229182 | 15084
Modern Electric Water Company | 96035 | 126651 |  |  | 222686 | 10020
Nespelem Valley Elec Coop, Inc | 17713.296 | 23299.5732 | 19747.8215 | 0 | 60886 | 1524
Northern Lights, Inc | 232021 | 47849 | 28127 | 0 | 307997 | 20162
Northern Wasco County PUD | 138890 | 19690 | 625830 |  | 784410 | 10112
NorthWestern Corporation | 757200.4068 | 1277993.3124 | 1001822.7789 |  | 3037016.4981 | 112016.9457
Ohop Mutual Light Company, Inc | 77776 | 4358 | 45 |  | 82179 | 4413
Okanogan County Elec Coop, Inc | 38314 | 19706 |  |  | 58020 | 3574
Orcas Power & Light Coop | 149472 | 59261 |  |  | 208733 | 15082
Oregon Trail El Cons Coop, Inc | 289676 | 250128 | 117674 |  | 657478 | 31254
Pacific Public Utility District No 2 | 178573 | 89854 | 23011 |  | 291438 | 17496
PacifiCorp | 7779810 | 7695254 | 5362692 | 15048 | 20852804 | 798332
Parkland Light & Water Company | 54913 | 58482 |  |  | 113395 | 4566
Peninsula Light Company | 481481 | 99867 |  |  | 581348 | 33335
Port Angeles City of | 123274 | 101550 | 44069 |  | 268893 | 10971
Portland General Electric Company | 7415759 | 7375419 | 4419370 | 10948 | 19221496 | 888123
PUD No 1 of Asotin County | 0 | 0.22469 | 0 | 0 | 247 | 3
PUD No 1 of Benton County | 698135 | 552107 | 490607 |  | 1740849 | 53744
PUD No 1 of Chelan County | 809774 | 486579 | 338664 |  | 1635017 | 50456
PUD No 1 of Clallam County | 439440 | 172619 | 20161 |  | 632220 | 31905
PUD No 1 of Clark County | 2364873 | 1335558 | 764602 |  | 4465033 | 208717
PUD No 1 of Cowlitz County | 711762 | 382495 | 3745632 | 0 | 4839889 | 50751
PUD No 1 of Douglas County | 423075 | 381532 | 201110 |  | 1005717 | 15755
PUD No 1 of Ferry County | 35666 | 10165 | 20895 | 0 | 66726 | 3507
PUD No 1 of Franklin County | 357358 | 398435 | 287041 |  | 1042834 | 27180
PUD No 1 of Grays Harbor Cnty | 466645 | 337185 | 152271 |  | 956101 | 42953
PUD No 1 of Jefferson County | 207266 | 69200 | 99970 |  | 376436 | 19877
PUD No 1 of Kittitas County | 59494.851 | 31191.6214 | 7214.5276 | 0 | 97901 | 4485
PUD No 1 of Klickitat County | 141628 | 111719 | 91160 |  | 344507 | 12710
PUD No 1 of Lewis County | 437275 | 218423 | 266679 |  | 922377 | 32385
PUD No 1 of Mason County | 59641.3137 | 16017.6863 | 0 | 0 | 75659 | 5293
PUD No 1 of Okanogan County | 290654 | 293747 | 14993 |  | 599394 | 21114
PUD No 1 of Pend Oreille Cnty | 145245 | 52432 | 802274 |  | 999951 | 9310
PUD No 1 of Skamania Co | 75435 | 28718 | 16411 | 0 | 120564 | 6101
PUD No 1 of Wahkiakum County | 29739.8738 | 11304.1262 | 0 | 0 | 41044 | 2539
PUD No 1 of Whatcom County |  |  | 220310 |  | 220310 | 1
PUD No 2 of Grant County | 765978 | 961590 | 3183187 |  | 4910755 | 50688
PUD No 3 of Mason County | 421592 | 186277 | 37814 | 0 | 645683 | 33841
Puget Sound Energy Inc | 10497389 | 9038758 | 3183911 | 5865 | 22725923 | 1149781
Raft River Rural Elec Coop Inc | 23537 | 47758 | 147957 | 0 | 219252 | 2616
Ravalli County Elec Coop, Inc | 132071 | 12293 | 9642 |  | 154006 | 10552
Riverside Electric Cooperative | 14844.7995 | 0 | 0 | 0 | 21311 | 594
Rupert City of | 35718 | 28569 | 13131 | 0 | 77418 | 3012
Salem Electric | 182733 | 108802 | 26211 |  | 317746 | 19822
Salmon River Electric Coop Inc | 31663 | 21865 | 44563 |  | 98091 | 2797
Seattle City of | 3000403 | 5021154 | 1051774 | 730 | 9074061 | 461523
Shell Energy North America (US), L.P. | 0 | 28651 | 1293212 | 0 | 1321863 | 10
Snohomish County PUD No 1 | 3566730 | 2386767 | 528243 | 0 | 6481740 | 350467
SolarCity Corporation | 23972 | 7512 | 0 | 0 | 31484 | 3840
South Side Electric, Inc | 24232.3489 | 0 | 0 | 0 | 58794 | 813
Surprise Valley Electrification Corp. | 50059 | 14920 | 70151 | 0 | 135130 | 6610
Tacoma City of | 1863660 | 328887 | 2424144 | 542 | 4617233 | 177725
Talen Energy Marketing, LLC |  | 341861 | 902796 |  | 1244657 | 12
Tanner Electric Coop | 58091 | 32589 |  |  | 90680 | 4911
Tenaska Power Services Co | 0 | 0 | 478403 | 0 | 478403 | 3
Tillamook Peoples Utility Dist | 232930 | 127363 | 109595 |  | 469888 | 21242
Tongue River Electric Coop Inc | 56751 | 12952 | 29557 |  | 99260 | 5026
Town of Eatonville | 16229.4389 | 10539.5686 | 0 | 0 | 26769 | 1231
Town of Ruston | 7475 | 0 | 0 | 0 | 7475 | 547
Town of Steilacoom | 30709 | 6306 |  |  | 37015 | 2963
Umatilla Electric Coop Assn | 166846 | 210511 | 2155160 |  | 2532517 | 15288
United Electric Co-op, Inc | 89525 | 63886 | 144902 |  | 298313 | 6736
USBIA-Mission Valley Power | 235022 | 127147 | 18016 | 0 | 380185 | 21462
Vera Irrigation District #15 | 142882 | 78028 |  |  | 220910 | 11897
Vigilante Electric Coop, Inc | 109302 | 7713 | 49483 |  | 166498 | 10060
WAPA-- Western Area Power Administration | 0 | 96630 | 26171 | 0 | 122801 | 15
Wasco Electric Coop, Inc | 49822 | 17192 | 39690 |  | 106704 | 4704
West Oregon Electric Coop Inc | 50619.7344 | 5044.7466 | 9013.519 | 0 | 64678 | 4390
Wells Rural Electric Co | 59432 | 65167 | 667363 | 0 | 791962 | 6136
Total Result | 65718496.9118 | 56967765.3825 | 54278997.7965 | 33133 | 177105194.4981 | 6694956.9457
| 7502.1115 | 6503.1696 | 6196.2326 | 3.7823 | 20217.488 | 764.2645
Chelan | 809774 | 486579 | 338664 | 0 | 1635017 | 50456
Grant | 765978 | 961590 | 3183187 | 0 | 4910755 | 50688
Douglas | 423075 | 381532 | 201110 | 0 | 1005717 | 15755
4.264%
|  | 8.44% |  |  | 9.759%
|  | 19847954.0701 |  |  | 69832176

## 2012 Sales
2012 Regional Sales Numbers
Source: "2012 Sales Source Data" Sheet Modifications: None Purpose: Aggregate data from utilities with multile rows in the original source data. For more info, see source sheet.
1 | 2 | 3 | 4 | 5 | 6 | 7
Data
UTILITY_NAME | Sum of Res Sales (MWh) | Sum of Com Sales (MWh) | Sum of Ind Sales (MWh) | Sum of Trans Sales (MWh) | Sum of Total Sales (MWh) | Sum of Total Consumers (n)
Alder Mutual Light Co, Inc | 4192.5981 | 428.4019 | 0 | 0 | 4621 | 278
Avista Corp | 3608625 | 3164732 | 2099648 | 0 | 8873005 | 360553
Beartooth Electric Coop, Inc | 44600 | 7810 | 2094 |  | 54504 | 5344
Benton Rural Electric Assn | 223469 | 118874 | 211980 |  | 554323 | 15188
Big Bend Electric Coop, Inc | 97757 | 395899 | 0 |  | 493656 | 8694
Big Flat Electric Coop Inc | 18204.5308 | 3790.4868 | 5053.9824 | 0 | 27049 | 1894
Big Horn County Elec Coop, Inc | 38911 | 20022 | 0 |  | 58933 | 3645
Big Horn Rural Electric Co | 354 | 2020 | 13736 |  | 16110 | 67
Blachly-Lane Cnty Coop El Assn | 51494 | 41345 | 65684 |  | 158523 | 3621
Black Hills Power Inc | 61 | 1519 | 48328 |  | 49908 | 35
Bonneville Power Admin |  | 863330 | 6882215 |  | 7745545 | 13
BP Energy Company |  | 0 | 852781 |  | 852781 | 3
Canby Utility Board | 78374 | 59383 | 30927 |  | 168684 | 6746
Central Electric Coop Inc | 440371 | 97063 | 109654 |  | 647088 | 31380
Central Lincoln People's Ut Dt | 433411 | 188055 | 689573 |  | 1311039 | 38375
City of Albion | 1903.3496 | 845.6504 | 0 | 0 | 2749 | 202
City of Ashland | 90862 | 81286 | 0 |  | 172148 | 11688
City of Bandon | 34629 | 27842 | 1333 |  | 63804 | 3759
City of Blaine | 24042 | 39249 | 9519 |  | 72810 | 3020
City of Bonners Ferry | 24225.0273 | 23244.7546 | 18576.2182 | 0 | 66046 | 2593
City of Burley | 46454 | 64345 | 0 | 0 | 110799 | 4514
City of Cascade Locks | 8082.5202 | 9656.4798 | 0 | 0 | 17739 | 808
City of Centralia | 117052 | 36015 | 107760 |  | 260827 | 9982
City of Cheney | 52056 | 70429 | 9741 |  | 132226 | 4925
City of Chewelah | 12568.3572 | 10231.6428 | 0 | 0 | 22800 | 1290
City of Coulee Dam | 9446.4928 | 7187.5072 | 0 | 0 | 16634 | 597
City of Declo | 1641.4379 | 994.3001 | 366.262 | 0 | 3002 | 134
City of Drain | 7479.5778 | 3461.0353 | 4817.3869 | 0 | 15758 | 677
City of Ellensburg | 75016 | 116613 | 10519 | 0 | 202148 | 9531
City of Forest Grove | 109097 | 20915 | 102541 |  | 232553 | 9110
City of Hermiston | 51129 | 53502 | 0 | 0 | 104631 | 5288
City of McCleary | 15655.4091 | 4308.0532 | 9721.5377 | 0 | 29685 | 1025
City of Milton | 41313.9366 | 17681.0634 | 0 | 0 | 58995 | 3399
City of Milton-Freewater | 60331 | 14487 | 30391 |  | 105209 | 4344
City of Minidoka | 827.8355 | 40.1645 | 0 | 0 | 868 | 48
City of Monmouth | 43642 | 3758 | 21919 |  | 69319 | 4268
City of Plummer | 9994.5608 | 8646.9 | 13794.5392 | 0 | 32436 | 995
City of Richland | 330864 | 346643 | 170011 |  | 847518 | 25727
City of Soda Springs | 13569.9547 | 13229.6254 | 368.4199 | 0 | 27168 | 1784
City of Springfield | 386504 | 262900 | 162504 |  | 811908 | 31695
City of Sumas | 5513.869 | 4826.1305 | 19159.0005 | 0 | 29499 | 690
City of Troy | 12816.6459 | 5649.7169 | 71.6372 | 0 | 18538 | 976
City of Weiser | 25177.6889 | 14221.4739 | 9836.8372 | 0 | 49236 | 2733
Clatskanie Peoples Util Dist | 72364 | 26226 | 872001 | 0 | 970591 | 4609
Clear Lake Cogeneration LP |  | 0 | 218452 |  | 218452 | 1
Clearwater Power Company | 128317 | 28244 | 24477 |  | 181038 | 10359
Columbia Basin Elec Cooperative, Inc | 41387 | 27649 | 35848 | 0 | 104884 | 3838
Columbia Power Coop Assn Inc | 13912 | 5034 | 5138 |  | 24084 | 1814
Columbia River Peoples Ut Dist | 211529 | 88068 | 161465 |  | 461062 | 18637
Columbia Rural Elec Assn, Inc | 48138 | 46909 | 203291 |  | 298338 | 4900
ConocoPhillips Company | 0 | 0 | 384715 | 0 | 384715 | 3
Constellation NewEnergy, Inc | 0 | 63284 | 0 | 0 | 63284 | 1
Consumers Power, Inc | 269083 | 104203 | 19419 |  | 392705 | 22014
Coos-Curry Electric Coop, Inc | 196349 | 94495 | 47835 |  | 338679 | 17452
Douglas Electric Coop, Inc | 120998 | 18649 | 6765 |  | 146412 | 9778
East End Mutual Elec Co Ltd | 15333.3333 | 7666.6667 | 0 | 0 | 23000 | 727
Elmhurst Mutual Power & Light Co | 220710 | 39861 | 0 |  | 260571 | 13935
Emerald People's Utility Dist | 280175 | 86512 | 204917 | 0 | 571604 | 20486
Eugene City of | 941922 | 872419 | 550270 | 0 | 2364611 | 89342
Fall River Rural Elec Coop Inc | 146967 | 129963 | 0 |  | 276930 | 15076
Farmers Electric Company, Ltd | 1875.4395 | 1975.1969 | 183.3636 | 0 | 4034 | 120
Fergus Electric Coop, Inc | 57000 | 138000 | 3000 |  | 198000 | 6146
Flathead Electric Coop Inc | 674819 | 427906 | 244791 |  | 1347516 | 61621
Glacier Electric Coop, Inc | 68147 | 81600 | 19394 |  | 169141 | 7471
Goldenwest Electric Coop, Inc | 5855.3944 | 773.6056 | 0 | 0 | 6629 | 721
Grand Electric Coop, Inc | 117 | 0 | 0 | 0 | 117 | 15
Harney Electric Coop, Inc | 17596 | 0 | 64794 |  | 82390 | 2413
Heyburn City of | 19715.932 | 6790.3992 | 13364.6688 | 0 | 39871 | 1500
Hill County Electric Coop, Inc | 39008 | 26909 | 59591 |  | 125508 | 3759
Hinson Power Company LLC | 0 | 0 | 8783 | 0 | 8783 | 1
Hood River Electric Coop | 53201 | 5606 | 49640 |  | 108447 | 3685
Idaho Cnty L&P Coop Assn, Inc | 40455.6486 | 8115.6695 | 197.6819 | 0 | 48769 | 3750
Idaho Falls City of | 279649 | 261215 | 87016 | 0 | 627880 | 26161
Idaho Power Co | 5039358 | 3864967 | 5180991 | 0 | 14085316 | 498282
Inland Power & Light Company | 615280 | 120409 | 117125 |  | 852814 | 38803
JP Morgan | 0 | 0 | 761031 | 0 | 761031 | 3
Kootenai Electric Coop Inc | 281910 | 102203 | 28505 | 0 | 412618 | 22368
Lakeview Light & Power | 114535 | 149774 | 0 |  | 264309 | 11434
Lane Electric Coop Inc | 191562 | 32356 | 3776 |  | 227694 | 12729
Lincoln Electric Coop, Inc | 71230 | 26060 | 11010 |  | 108300 | 5383
Lost River Electric Coop Inc | 31934.353 | 4667.0573 | 41280.5897 | 0 | 77882 | 2621
Lower Valley Energy Inc | 13073 | 2690 | 46527 |  | 62290 | 1621
Lower Yellowstone R E A, Inc | 37263 | 29379 | 86946 |  | 153588 | 4566
Marias River Electric Coop Inc | 29843 | 56393 | 0 |  | 86236 | 3838
McCone Electric Coop Inc | 43344 | 21603 | 1744 |  | 66691 | 5123
McKenzie Electric Coop Inc | 749 | 1 | 0 | 0 | 750 | 125
McMinnville City of | 204187 | 177463 | 335477 | 0 | 717127 | 16270
Midstate Electric Coop, Inc | 231394 | 112104 | 28081 |  | 371579 | 18215
Mid-Yellowstone Elec Coop, Inc | 13438 | 3713 | 11883 |  | 29034 | 1956
Missoula Electric Coop, Inc | 150332 | 40935 | 18593 | 0 | 209860 | 14072
Modern Electric Water Company | 96953 | 112103 | 0 |  | 209056 | 9855
Montana-Dakota Utilities Co | 190509 | 251430 | 320527 | 0 | 762466 | 25011
Nespelem Valley Elec Coop, Inc | 21214.3563 | 14765.9723 | 13528.6714 | 0 | 49509 | 1563
Noble Americas Energy Solutions LLC | 0 | 904381 | 434140 | 0 | 1338521 | 47
Northern Lights, Inc | 207105 | 41143 | 66628 | 0 | 314876 | 18543
Northern Wasco County PUD | 139695 | 17549 | 393231 |  | 550475 | 9855
NorthWestern Corporation | 2354708 | 3247735 | 2986868 | 0 | 8589311 | 341229
NorVal Electric Cooperative, Inc | 29622.1978 | 17547.1567 | 5380.6456 | 0 | 52550 | 3255
Ohop Mutual Light Company, Inc | 74133 | 3897 | 52 |  | 78082 | 4188
Okanogan County Elec Coop, Inc | 37438 | 16803 | 0 |  | 54241 | 3512
Orcas Power & Light Coop | 140026 | 55140 | 0 |  | 195166 | 14685
Oregon Trail El Cons Coop, Inc | 280932 | 244065 | 106611 |  | 631608 | 30309
Pacific Public Utility District No 2 | 179572 | 83201 | 23082 |  | 285855 | 17261
PacifiCorp | 7677508 | 7031959 | 5799005 | 16638 | 20525110 | 760106
Park Electric Coop Inc | 65094 | 7610 | 81627 |  | 154331 | 5558
Parkland Light & Water Company | 55916 | 60861 | 0 |  | 116777 | 4453
Peninsula Light Company | 423183 | 156492 | 0 | 0 | 579675 | 30865
Port Angeles City of | 133310 | 112336 | 476055 |  | 721701 | 11527
Portland General Electric Company | 7505404 | 7321642 | 4355931 | 8166 | 19191143 | 827467
Powder River Energy Corporation | 532 | 13020 | 96387 |  | 109939 | 283
PPL EnergyPlus LLC | 0 | 86404 | 2128598 | 0 | 2215002 | 14
Public Utility District No 1 | 30472.0617 | 10611.9383 | 0 | 0 | 41084 | 2400
PUD No 1 of Asotin County | 0 | 282 | 0 | 0 | 282 | 3
PUD No 1 of Benton County | 668018 | 520945 | 456313 |  | 1645276 | 48710
PUD No 1 of Chelan County | 762266 | 469223 | 310897 | 0 | 1542386 | 47911
PUD No 1 of Clallam County | 446567 | 172056 | 28879 |  | 647502 | 30470
PUD No 1 of Clark County | 2317528 | 1296346 | 740918 | 0 | 4354792 | 186577
PUD No 1 of Cowlitz County | 754607 | 381027 | 4015094 |  | 5150728 | 48306
PUD No 1 of Douglas County | 392981 | 254538 | 104578 |  | 752097 | 15280
PUD No 1 of Ferry County | 38511 | 9664 | 54878 | 0 | 103053 | 3343
PUD No 1 of Franklin County | 336205 | 364908 | 284551 |  | 985664 | 24248
PUD No 1 of Grays Harbor Cnty | 497856 | 301746 | 176342 |  | 975944 | 41413
PUD No 1 of Kittitas County | 56179.8244 | 29453.6382 | 6812.5374 | 0 | 92446 | 4189
PUD No 1 of Klickitat County | 139822 | 98078 | 78032 |  | 315932 | 12203
PUD No 1 of Lewis County | 457085 | 217839 | 249638 |  | 924562 | 31047
PUD No 1 of Mason County | 59327.5739 | 15933.4261 | 0 | 0 | 75261 | 5112
PUD No 1 of Okanogan County | 289640 | 270703 | 20584 |  | 580927 | 20679
PUD No 1 of Pend Oreille Cnty | 138253 | 49850 | 814788 |  | 1002891 | 8777
PUD No 1 of Skamania Co | 74327 | 21912 | 26953 |  | 123192 | 5841
PUD No 1 of Whatcom County |  | 0 | 195272 |  | 195272 | 1
PUD No 2 of Grant County | 739941 | 720162 | 2469920 |  | 3930023 | 46602
PUD No 3 of Mason County | 425976 | 185203 | 52358 |  | 663537 | 32249
Puget Sound Energy Inc | 10869292 | 9158121 | 3087934 | 3694 | 23119041 | 1089287
Raft River Rural Elec Coop Inc | 22408 | 38124 | 156439 | 0 | 216971 | 2494
Ravalli County Elec Coop, Inc | 130987 | 9461 | 2743 | 0 | 143191 | 9794
Riverside Electric Cooperative | 20000 | 0 | 0 | 0 | 20000 | 540
Rupert City of | 36354 | 24800 | 11920 |  | 73074 | 2613
Salem Electric | 183577 | 102690 | 25806 |  | 312073 | 18578
Salmon River Electric Coop Inc | 32666 | 19882 | 225195 |  | 277743 | 2694
Seattle City of | 3146951 | 5237477 | 1081568 | 646 | 9466642 | 402608
Shell Energy North America (US), L.P. | 0 | 0 | 604899 | 0 | 604899 | 2
Sheridan Electric Coop, Inc | 34059 | 67399 | 4435 |  | 105893 | 4124
Sierra Pacific Industries Inc |  | 0 | 37537 |  | 37537 | 1
Snohomish County PUD No 1 | 3531333 | 2364872 | 639379 |  | 6535584 | 325849
South Side Electric, Inc | 27737.648 | 0 | 29768.352 | 0 | 57506 | 1231
Southeast Electric Coop, Inc | 16224.6929 | 791.4733 | 9264.8338 | 0 | 26281 | 1960
Sun River Electric Coop, Inc | 45248 | 15275 | 28919 |  | 89442 | 5610
Surprise Valley Electrification Corp. | 15827 | 3872 | 15105 | 0 | 34804 | 1763
Tacoma City of | 1898579 | 334921 | 2505933 | 2632 | 4742065 | 169018
Tanner Electric Coop | 56449 | 35279 | 0 |  | 91728 | 4558
Tillamook Peoples Utility Dist | 229065 | 122911 | 108791 |  | 460767 | 20585
Tongue River Electric Coop Inc | 51389 | 12602 | 19184 |  | 83175 | 4933
Town of Eatonville | 15557.9615 | 12187.0385 | 0 | 0 | 27745 | 1170
Town of Ruston | 6216 | 0 | 0 | 0 | 6216 | 489
Town of Steilacoom | 30911 | 7376 | 0 |  | 38287 | 2863
Umatilla Electric Coop Assn | 164377 | 167374 | 641630 |  | 973381 | 14254
United Electric Co-op, Inc | 86074 | 45738 | 126888 |  | 258700 | 6168
USBIA-Mission Valley Power | 217040 | 121085 | 15177 | 0 | 353302 | 20893
Vera Irrigation District #15 | 136247 | 84015 | 0 |  | 220262 | 10176
Vigilante Electric Coop, Inc | 94938 | 65735 | 0 | 0 | 160673 | 9145
Wasco Electric Coop, Inc | 49264 | 15986 | 42057 |  | 107307 | 4633
West Oregon Electric Coop Inc | 53372.2872 | 5319.0651 | 9503.6477 | 0 | 68195 | 4251
Western Area Power Administration |  | 105218 | 0 |  | 105218 | 22
Yellowstone Valley Elec Co-op | 185958 | 52012 | 8869 |  | 246839 | 17494
Total Result | 67312293.4963 | 56990357.6905 | 58486344.8131 | 31776 | 182820772 | 6524129

## 2005 Sales
2005 Regional Sales Numbers
Source: "2005 Sales Source Data" Sheet Modifications: None Purpose: Aggregate data from utilities with multile rows in the original source data. For more info, see source sheet.
1 | 2 | 3 | 4 | 5 | 6 | 7
Data
UTILITY_NAME | Sum of Residential Sales (MWh) | Sum of Commercial | Sum of Industrial/Other | Sum of Dummy Column - Only used to keep column numbers consistent between "20XX Sales" Sheets | Sum of Annual Energy MWh | Sum of Total Number of Customers
Alder Mutual Light Co, Inc | 3285 |  |  | 0 | 3285 | 246
Avista Corp | 3419532 | 4459916 | 4459916 | 0 | 12339364 | 294036
Benton Rural Electric Assn | 207909 | 110838.4255 | 11682.5745 | 0 | 330430 | 12055
Big Bend Electric Coop, Inc | 90453 | 3508.7517 | 309322.2483 | 0 | 403284 | 6706
Blachly-Lane Cnty Coop El Assn | 51101 | 45837.1867 | 19551.4066 | 0 | 136041 | 3383
Canby Utility Board | 73142 | 62332.9089 | 18731.0911 | 0 | 154206 | 6247
Central Electric Coop Inc | 400482 |  |  | 0 | 398735 | 27225
Central Lincoln People's Ut Dt | 414445 | 543847.6325 | 334076.3675 | 0 | 1292369 | 36841
City of Albion | 1908 | 1054 | 0 | 0 | 2962 | 139
City of Ashland | 87675 | 81481 | 0 | 0 | 169156 | 11310
City of Bandon | 31794 | 23209.2976 | 1753.8512 | 0 | 58511 | 3131
City of Blaine | 21123 | 28271.0339 | 7248.9831 | 0 | 63892 | 2761
City of Bonners Ferry | 23131 | 27276.6808 | 10046.6596 | 0 | 70501 | 2378
City of Burley | 42664 | 55034 | 0 | 0 | 97698 | 4309
City of Cascade Locks | 8334 | 12005 | 0 | 0 | 20339 | 569
City of Cashmere | 19327 | 17624.5714 | 18731.4286 | 0 | 55683 | 1168
City of Centralia | 112752 | 116584 | 0 | 0 | 229336 | 9580
City of Cheney | 42997 | 54288.6364 | 17372.3636 | 0 | 114658 | 4256
City of Chewelah | 11017 | 10076 | 0 | 0 | 21093 | 1265
City of Coulee Dam | 9810 | 8234 | 0 | 0 | 18044 | 603
City of Declo | 1257 | 78.3636 | 783.6364 | 0 | 2119 | 131
City of Drain | 7502 | 6208.9544 | 6758.0456 | 0 | 20469 | 667
City of Ellensburg | 59644 | 128482.4236 | 1818.5764 | 0 | 189945 | 8422
City of Forest Grove | 105163 | 46640.8136 | 98191.1864 | 0 | 249995 | 8751
City of Hermiston | 49525 | 55502 | 0 | 0 | 105027 | 5165
City of McCleary | 12685 | 16662.0594 | 5462.9703 | 0 | 40273 | 1016
City of Milton | 39390 | 18280 | 0 | 0 | 57670 | 3332
City of Milton-Freewater | 59932 | 24920.3911 | 25016.6089 | 0 | 109869 | 4854
City of Minidoka | 473 | 93 | 0 | 0 | 566 | 43
City of Monmouth | 34470 | 2858.7002 | 18389.2998 | 0 | 55718 | 3645
City of Plummer | 9016 | 14488.5106 | 6791.4894 | 0 | 30296 | 775
City of Richland | 295048 | 424367.4966 | 33365.5034 | 0 | 752781 | 21020
City of Soda Springs | 12349 | 9570.9792 | 644.5104 | 0 | 23209 | 1745
City of Springfield | 382311 | 374423.3882 | 26482.6118 | 0 | 783217 | 30774
City of Sumas | 4002 | 7077.2958 | 16850.7042 | 0 | 27930 | 595
City of Troy | 9724 |  |  | 0 | 9724 | 786
City of Weiser | 24636 | 29715.398 | 798.801 | 0 | 55949 | 2772
Clatskanie Peoples Util Dist | 67769 | 794740.6452 | 117739.3548 | 0 | 980249 | 4408
Clearwater Power Company | 111456 | 12046.0155 | 33657.9845 | 0 | 157160 | 9754
Columbia Basin Elec Cooperative, Inc | 37000 | 4923.7388 | 26901.6306 | 0 | 95727 | 3655
Columbia Power Coop Assn Inc | 13655 | 359.7509 | 4845.6245 | 0 | 23706 | 1736
Columbia River Peoples Ut Dist | 188505 | 189105.8081 | 110588.1919 | 0 | 488199 | 17718
Columbia Rural Elec Assn, Inc | 43104 | 6599.331 | 70429.8345 | 0 | 190563 | 3492
Consumers Power, Inc | 251024 | 24875.245 | 341268.755 | 0 | 617168 | 19956
Coos-Curry Electric Coop, Inc | 182058 | 102562 | 0 | 0 | 284620 | 16456
Douglas Electric Coop, Inc | 113405 | 545.6379 | 4998.3621 | 0 | 118949 | 9369
East End Mutual Elec Co Ltd | 13016 |  |  | 0 | 13016 | 559
Elmhurst Mutual Power & Light Co | 211302 |  |  | 0 | 211302 | 12699
Emerald People's Utility Dist | 251360 | 176829.539 | 15802.461 | 0 | 443992 | 18522
Eugene City of | 960623 | 1687272.9204 | 15278.0796 | 0 | 2663174 | 84137
Fall River Rural Elec Coop Inc | 116956 | 8189.0455 | 49252.9545 | 0 | 174398 | 12605
Farmers Electric Company, Ltd | 1892 |  |  | 0 | 1892 | 99
Flathead Electric Coop Inc | 568902 | 107394.6104 | 704064.3896 | 0 | 1380361 | 50610
Glacier Electric Coop, Inc | 61272 | 23817.3906 | 59706.6094 | 0 | 144796 | 7138
Harney Electric Coop, Inc | 27821 | 1477.6204 | 96523.6898 | 0 | 222346 | 2575
Heyburn City of | 16393 | 10266.2143 | 1115.8929 | 0 | 28891 | 1182
Hood River Electric Coop | 47944 | 0 | 0 | 0 | 47944 | 3489
Idaho Cnty L&P Coop Assn, Inc | 33231 | 1435.169 | 925.9155 | 0 | 36518 | 3274
Idaho Falls City of | 272395 | 362359.1154 | 16340.8846 | 0 | 651095 | 24277
Idaho Power Co | 4760275 | 3582126.3588 | 3582126.3588 | 0 | 11924527.7176 | 373603
Inland Power & Light Company | 545226 |  |  | 0 | 473000 | 32935
Kootenai Electric Coop Inc | 243294 |  |  | 0 | 233093 | 19665
Lakeview Light & Power | 138820 |  |  | 0 | 138820 | 7806
Lane Electric Coop Inc | 184786 | 9567.8638 | 8467.1362 | 0 | 202821 | 12187
Lincoln Electric Coop, Inc | 61753 | 1242.8445 | 39186.1555 | 0 | 102182 | 4413
Lost River Electric Coop Inc | 25537 | 431.5364 | 12412.7318 | 0 | 50794 | 2386
Lower Valley Energy Inc | 329905 |  |  | 0 | 329905 | 18097
McMinnville City of | 192092 | 549580.4591 | 83244.5409 | 0 | 824917 | 15418
Midstate Electric Coop, Inc | 208436 | 7811.5506 | 43234.4494 | 0 | 259482 | 16908
Missoula Electric Coop, Inc | 135638 |  |  | 0 | 135638 | 11681
Modern Electric Water Company | 89999 |  |  | 0 | 89999 | 7942
Nespelem Valley Elec Coop, Inc | 17605 | 2068.7912 | 9257.6044 | 0 | 38189 | 1817
Northern Lights, Inc | 180512 | 8588.9281 | 8472.0719 | 0 | 197573 | 16520
Northern Wasco County PUD | 130575 | 10997.6355 | 100856.3645 | 0 | 242429 | 9486
NorthWestern Corporation | 567652.86 | 3225689.07 | 3225689.07 | 0 | 7019031 | 68294.88
Ohop Mutual Light Company, Inc | 69585 |  |  | 0 | 69585 | 3851
Okanogan County Elec Coop, Inc | 30797 | 0 | 0 | 0 | 30797 | 3195
Orcas Power & Light Coop | 131805 | 6402.6247 | 523.3753 | 0 | 138731 | 12544
Oregon Trail El Cons Coop, Inc | 246248 |  |  | 0 | 246248 | 24046
Pacific Public Utility District No 2 | 165674 | 113245.279 | 2138.721 | 0 | 281058 | 16487
PacifiCorp | 8004700 | 6934893.5 | 3060406.5 | 0 | 18000000 | 632304
Parkland Light & Water Company | 52894 |  |  | 0 | 52894 | 3866
Peninsula Light Company | 386574 |  |  | 0 | 386574 | 25787
Port Angeles City of | 130727 | 511642.9882 | 23034.0118 | 0 | 665404 | 10443
Portland General Electric Company | 7322964 | 7075000 | 4474000 | 0 | 18432528 | 680093
PUD No 1 of Benton County | 622639 | 311006.9418 | 668862.0582 | 0 | 1602508 | 44389
PUD No 1 of Chelan County | 665318 | 174800.118 | 582977.882 | 0 | 1423096 | 43705
PUD No 1 of Clallam County | 402235 | 52933.0912 | 140737.9088 | 0 | 595906 | 28444
PUD No 1 of Clark County | 2230688 | 1984336.2823 | 74604.7177 | 0 | 4289629 | 173548
PUD No 1 of Cowlitz County | 725791 | 2743381.549 | 915688.451 | 0 | 4384861 | 46702
PUD No 1 of Douglas County | 338778 | 25197.4307 | 186588.5693 | 0 | 550564 | 16931
PUD No 1 of Ferry County | 32911 | 8967.2297 | 20399.3851 | 0 | 82677 | 3221
PUD No 1 of Franklin County | 275018 | 526516.1462 | 8893.8538 | 0 | 810428 | 23703
PUD No 1 of Grays Harbor Cnty | 486892 | 260459 | 245479 | 0 | 992830 | 41059
PUD No 1 of Kittitas County | 44314 | 1515.3826 | 16013.6174 | 0 | 61843 | 3690
PUD No 1 of Klickitat County | 119451 | 157838.1366 | 4960.8634 | 0 | 282250 | 11156
PUD No 1 of Lewis County | 395293 | 312370.7685 | 100617.2315 | 0 | 808281 | 28837
PUD No 1 of Mason County | 47960 | 13865 | 0 | 0 | 61825 | 4931
PUD No 1 of Okanogan County | 262901 |  |  | 0 | 216486 | 19382
PUD No 1 of Pend Oreille Cnty | 131586 | 723974.5072 | 121530.4928 | 0 | 977091 | 8249
PUD No 1 of Skamania Co | 67302 | 23089.5131 | 16283.7434 | 0 | 122959 | 5548
PUD No 1 of Whatcom County | 0 |  | 207228 | 0 | 207228 | 1
PUD No 1 Wahkiakum County | 26264 | 9815 | 0 | 0 | 36079 | 2262
PUD No 2 of Grant County | 669081 | 141591.6864 | 2207938.3136 | 0 | 3018611 | 41722
PUD No 3 of Mason County | 369780 | 246247.5157 | 2228.4843 | 0 | 618256 | 30830
Puget Sound Energy Inc | 10722240 | 8917680 | 1480440 | 0 | 23183514 | 1160937
Raft River Rural Elec Coop Inc | 36000 | 2332.2489 | 80422.3756 | 0 | 199177 | 4014
Ravalli County Elec Coop, Inc | 115686 |  |  | 0 | 115686 | 8927
Rupert City of | 36280 | 40862 | 0 | 0 | 77142 | 2729
Salem Electric | 176428 |  |  | 0 | 176428 | 15460
Salmon River Electric Coop Inc | 26881 | 245171.0558 | 13851.4721 | 0 | 272874 | 2307
Seattle City of | 2948779 | 5533365.9469 | 679321.0531 | 0 | 9161466 | 375865
Snohomish County PUD No 1 | 3188146 | 2950413.3322 | 166616.6678 | 0 | 6305176 | 300176
South Side Electric, Inc | 24662 | 0 | 0 | 0 | 24662 | 880
Surprise Valley Electrification Corp. | 46712 |  |  | 0 | 46712 | 3763
Tacoma City of | 1760110 | 644695.9982 | 2217847.0018 | 0 | 4622653 | 162968
Tanner Electric Coop | 51533 |  |  | 0 | 41706 | 4576
Tillamook Peoples Utility Dist | 208751 | 186282.0573 | 7150.9427 | 0 | 402184 | 19208
Town of Eatonville | 14697 | 9595 | 0 | 0 | 24292 | 1582
Town of Ruston | 5058 | 129 | 0 | 0 | 5187 | 418
Town of Steilacoom | 30517 | 7216 | 0 | 0 | 37733 | 2803
Umatilla Electric Coop Assn | 153858 | 401524.4952 | 42521.5048 | 0 | 597904 | 11614
United Electric Co-op, Inc | 83316 | 0 | 0 | 0 | 83316 | 5075
USBIA-Mission Valley Power | 194681 |  |  | 0 | 194681 | 13609
Vera Irrigation District #15 | 124864 | 76174 | 0 | 0 | 201038 | 9193
Vigilante Electric Coop, Inc | 79323 |  |  | 0 | 79323 | 7057
Wasco Electric Coop, Inc | 46912 | 262.5589 | 26236.4411 | 0 | 73411 | 5303
Wells Rural Electric Co | 45224 |  |  | 0 | 45224 | 4037
West Oregon Electric Coop Inc | 49161 | 5850.9083 | 6182.0917 | 0 | 61194 | 4217
Total Result | 62209185.86 | 59114338.0276 | 32033898.7476 | 0 | 155212720.7176 | 5567213.88

## 7P Data
7P Data
Source: "7P Source Data" Sheet Modifications: None Purpose: Sum substation counts for utilities which had multiple rows in the 7P "RegionWideSubstations" sheet. For more info, see source sheet.
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
Data
UTILITY_NAME | Sum of Number of Substations 2005 | Sum of No. Subs Res/Comm 2005 | Sum of No. Subs Res/Comm in 2012 | Sum of Industrial Subs 2005 | Sum of ECM1 CVRf | Sum of ECM1 %dV | Sum of ECM2 %dV | Sum of ECM2 CVRf | Sum of ECM3 %dV | Sum of ECM3 CVRf
Alder Mutual Light Co, Inc | 1 | 1 | 1 | 0 | 0.55 | 0.015 | 0.024 | 0.561 | 0.029 | 0.57222
Avista Corp | 122 | 122 | 122 | 0 | 0.924 | 0.015 | 0.02 | 0.94248 | 0.025 | 0.96133
Benton Rural Electric Assn | 1.8672 | 2 | 2 | -0.13276 | 0.55 | 0.015 | 0.02 | 0.561 | 0.025 | 0.57222
Big Bend Electric Coop, Inc | 2.2789 | 2 | 6 | 0.27893 | 0.55 | 0.015 | 0.02 | 0.561 | 0.025 | 0.57222
Blachly-Lane Cnty Coop El Assn | 1 | 1 | 1 | 0 | 0.55 | 0.015 | 0.024 | 0.561 | 0.029 | 0.57222
Canby Utility Board | 1 | 1 | 1 | 0 | 0.55 | 0.02 | 0.029 | 0.561 | 0.034 | 0.57222
Central Electric Coop Inc | 2.2532 | 2 | 2 | 0.25322 | 0.55 | 0.015 | 0.02 | 0.561 | 0.025 | 0.57222
Central Lincoln People's Ut Dt | 7.3031 | 7 | 7 | 0.30308 | 0.55 | 0.02 | 0.025 | 0.561 | 0.03 | 0.57222
City of Albion | 1 | 1 | 1 | 0 | 0.55 | 0.02 | 0.029 | 0.561 | 0.034 | 0.57222
City of Ashland | 1 | 1 | 1 | 0 | 0.55 | 0.02 | 0.029 | 0.561 | 0.034 | 0.57222
City of Bandon | 3 | 3 | 1 | 0 | 0.55 | 0.02 | 0.029 | 0.561 | 0.034 | 0.57222
City of Blaine | 1 | 1 | 1 | 0 | 0.55 | 0.02 | 0.029 | 0.561 | 0.034 | 0.57222
City of Bonners Ferry | 1 | 1 | 1 | 0 | 0.55 | 0.02 | 0.029 | 0.561 | 0.034 | 0.57222
City of Burley | 1 | 1 | 1 | 0 | 0.55 | 0.02 | 0.029 | 0.561 | 0.034 | 0.57222
City of Cascade Locks | 1 | 1 | 1 | 0 | 0.55 | 0.02 | 0.029 | 0.561 | 0.034 | 0.57222
City of Cashmere | 1 | 1 | 1 | 0 | 0.55 | 0.02 | 0.029 | 0.561 | 0.034 | 0.57222
City of Centralia | 1.296 | 1 | 1 | 0.29596 | 0.55 | 0.02 | 0.025 | 0.561 | 0.03 | 0.57222
City of Cheney | 1 | 1 | 1 | 0 | 0.55 | 0.02 | 0.029 | 0.561 | 0.034 | 0.57222
City of Chewelah | 1 | 1 | 1 | 0 | 0.55 | 0.02 | 0.029 | 0.561 | 0.034 | 0.57222
City of Coulee Dam | 1 | 1 | 1 | 0 | 0.55 | 0.02 | 0.029 | 0.561 | 0.034 | 0.57222
City of Declo | 1 | 1 | 1 | 0 | 0.55 | 0.02 | 0.029 | 0.561 | 0.034 | 0.57222
City of Drain | 1 | 1 | 1 | 0 | 0.55 | 0.02 | 0.029 | 0.561 | 0.034 | 0.57222
City of Ellensburg | 1.0734 | 1 | 1 | 0.073365 | 0.55 | 0.02 | 0.029 | 0.561 | 0.034 | 0.57222
City of Forest Grove | 1.4127 | 1 | 1 | 0.4127 | 0.55 | 0.02 | 0.025 | 0.561 | 0.03 | 0.57222
City of Hermiston | 1 | 1 | 1 | 0 | 0.55 | 0.02 | 0.029 | 0.561 | 0.034 | 0.57222
City of McCleary | 1 | 1 | 1 | 0 | 0.55 | 0.02 | 0.029 | 0.561 | 0.034 | 0.57222
City of Milton | 1 | 1 | 1 | 0 | 0.55 | 0.02 | 0.029 | 0.561 | 0.034 | 0.57222
City of Milton-Freewater | 1 | 1 | 1 | 0 | 0.55 | 0.02 | 0.029 | 0.561 | 0.034 | 0.57222
City of Minidoka | 1 | 1 | 1 | 0 | 0.55 | 0.02 | 0.029 | 0.561 | 0.034 | 0.57222
City of Monmouth | 1 | 1 | 1 | 0 | 0.55 | 0.02 | 0.029 | 0.561 | 0.034 | 0.57222
City of Plummer | 1 | 1 | 1 | 0 | 0.55 | 0.02 | 0.029 | 0.561 | 0.034 | 0.57222
City of Richland | 4.2539 | 4 | 4 | 0.25391 | 0.55 | 0.02 | 0.025 | 0.561 | 0.03 | 0.57222
City of Soda Springs | 1 | 1 | 1 | 0 | 0.55 | 0.02 | 0.029 | 0.561 | 0.034 | 0.57222
City of Springfield | 4.4259 | 4 | 4 | 0.4259 | 0.55 | 0.02 | 0.025 | 0.561 | 0.03 | 0.57222
City of Sumas | 1 | 1 | 1 | 0 | 0.55 | 0.02 | 0.029 | 0.561 | 0.034 | 0.57222
City of Troy | 1 | 1 | 1 | 0 | 0.55 | 0.02 | 0.029 | 0.561 | 0.034 | 0.57222
City of Weiser | 1 | 1 | 1 | 0 | 0.55 | 0.02 | 0.029 | 0.561 | 0.034 | 0.57222
Clatskanie Peoples Util Dist | 5.5393 | 5 | 1 | 0.53931 | 0.55 | 0.015 | 0.02 | 0.561 | 0.025 | 0.57222
Clearwater Power Company | 1 | 1 | 1 | 0 | 0.55 | 0.015 | 0.024 | 0.561 | 0.029 | 0.57222
Columbia Basin Elec Cooperative, Inc | 1 | 1 | 1 | 0 | 0.55 | 0.015 | 0.024 | 0.561 | 0.029 | 0.57222
Columbia Power Coop Assn Inc | 1 | 1 | 1 | 0 | 0.55 | 0.015 | 0.024 | 0.561 | 0.029 | 0.57222
Columbia River Peoples Ut Dist | 7 | 6 | 6 | 1 | 0.55 | 0.015 | 0.02 | 0.561 | 0.025 | 0.57222
Columbia Rural Elec Assn, Inc | 1.0769 | 1 | 1 | 0.076857 | 0.55 | 0.015 | 0.024 | 0.561 | 0.029 | 0.57222
Consumers Power, Inc | 3.4876 | 3 | 4 | 0.48757 | 0.55 | 0.015 | 0.02 | 0.561 | 0.025 | 0.57222
Coos-Curry Electric Coop, Inc | 1.6084 | 1 | 1 | 0.60837 | 0.55 | 0.015 | 0.02 | 0.561 | 0.025 | 0.57222
Douglas Electric Coop, Inc | 1 | 1 | 1 | 0 | 0.55 | 0.015 | 0.024 | 0.561 | 0.029 | 0.57222
East End Mutual Elec Co Ltd | 1 | 1 | 1 | 0 | 0.55 | 0.015 | 0.024 | 0.561 | 0.029 | 0.57222
Elmhurst Mutual Power & Light Co | 1.1941 | 1 | 1 | 0.19405 | 0.55 | 0.015 | 0.02 | 0.561 | 0.025 | 0.57222
Emerald People's Utility Dist | 9 | 8 | 8 | 1 | 0.55 | 0.015 | 0.02 | 0.561 | 0.025 | 0.57222
Eugene City of | 34 | 31 | 31 | 3 | 0.77 | 0.02 | 0.025 | 0.7854 | 0.03 | 0.80111
Fall River Rural Elec Coop Inc | 1 | 1 | 2 | 0 | 0.55 | 0.015 | 0.024 | 0.561 | 0.029 | 0.57222
Farmers Electric Company, Ltd | 1 | 1 | 1 | 0 | 0.55 | 0.015 | 0.024 | 0.561 | 0.029 | 0.57222
Flathead Electric Coop Inc | 7.8003 | 8 | 11 | -0.19968 | 0.55 | 0.01 | 0.015 | 0.561 | 0.02 | 0.57222
Glacier Electric Coop, Inc | 1 | 1 | 1 | 0 | 0.55 | 0.015 | 0.024 | 0.561 | 0.029 | 0.57222
Harney Electric Coop, Inc | 1.2565 | 1 | 1 | 0.25646 | 0.55 | 0.015 | 0.02 | 0.561 | 0.025 | 0.57222
Heyburn City of | 1 | 1 | 1 | 0 | 0.55 | 0.02 | 0.029 | 0.561 | 0.034 | 0.57222
Hood River Electric Coop | 1 | 1 | 1 | 0 | 0.55 | 0.015 | 0.024 | 0.561 | 0.029 | 0.57222
Idaho Cnty L&P Coop Assn, Inc | 1 | 1 | 1 | 0 | 0.55 | 0.015 | 0.024 | 0.561 | 0.029 | 0.57222
Idaho Falls City of | 3.6793 | 3 | 3 | 0.67929 | 0.55 | 0.02 | 0.025 | 0.561 | 0.03 | 0.57222
Idaho Power Co | 209 | 188 | 194 | 21 | 0.451 | 0.0286 | 0.0336 | 0.46002 | 0.0386 | 0.46922
Inland Power & Light Company | 2.6729 | 2 | 2 | 0.67289 | 0.55 | 0.015 | 0.02 | 0.561 | 0.025 | 0.57222
Kootenai Electric Coop Inc | 1.3172 | 1 | 1 | 0.31719 | 0.55 | 0.015 | 0.02 | 0.561 | 0.025 | 0.57222
Lakeview Light & Power | 1 | 1 | 1 | 0 | 0.55 | 0.015 | 0.024 | 0.561 | 0.029 | 0.57222
Lane Electric Coop Inc | 1.1461 | 1 | 1 | 0.14613 | 0.55 | 0.015 | 0.024 | 0.561 | 0.029 | 0.57222
Lincoln Electric Coop, Inc | 1 | 1 | 1 | 0 | 0.55 | 0.015 | 0.024 | 0.561 | 0.029 | 0.57222
Lost River Electric Coop Inc | 1 | 1 | 1 | 0 | 0.55 | 0.015 | 0.024 | 0.561 | 0.029 | 0.57222
Lower Valley Energy Inc | 1.8643 | 2 | 2 | -0.13573 | 0.55 | 0.015 | 0.02 | 0.561 | 0.025 | 0.57222
McMinnville City of | 5 | 5 | 5 | 0 | 0.55 | 0.02 | 0.025 | 0.561 | 0.03 | 0.57222
Midstate Electric Coop, Inc | 1.4663 | 1 | 1 | 0.46631 | 0.55 | 0.015 | 0.02 | 0.561 | 0.025 | 0.57222
Missoula Electric Coop, Inc | 1 | 1 | 1 | 0 | 0.55 | 0.015 | 0.024 | 0.561 | 0.029 | 0.57222
Modern Electric Water Company | 1 | 1 | 2 | 0 | 0.55 | 0.015 | 0.024 | 0.561 | 0.029 | 0.57222
Nespelem Valley Elec Coop, Inc | 1 | 1 | 1 | 0 | 0.55 | 0.015 | 0.024 | 0.561 | 0.029 | 0.57222
Northern Lights, Inc | 1.1165 | 1 | 1 | 0.11647 | 0.55 | 0.015 | 0.024 | 0.561 | 0.029 | 0.57222
Northern Wasco County PUD | 1.3699 | 1 | 1 | 0.36995 | 0.55 | 0.015 | 0.02 | 0.561 | 0.025 | 0.57222
NorthWestern Corporation | 39.664 | 32 | 40 | 7.664 | 0.55 | 0.01 | 0.015 | 0.561 | 0.02 | 0.57222
Ohop Mutual Light Company, Inc | 1 | 1 | 1 | 0 | 0.55 | 0.015 | 0.024 | 0.561 | 0.029 | 0.57222
Okanogan County Elec Coop, Inc | 1 | 1 | 1 | 0 | 0.55 | 0.015 | 0.024 | 0.561 | 0.029 | 0.57222
Orcas Power & Light Coop | 5 | 5 | 6 | 0 | 0.55 | 0.015 | 0.024 | 0.561 | 0.029 | 0.57222
Oregon Trail El Cons Coop, Inc | 1.3915 | 1 | 2 | 0.39153 | 0.55 | 0.015 | 0.02 | 0.561 | 0.025 | 0.57222
Pacific Public Utility District No 2 | 1.5882 | 1 | 1 | 0.58824 | 0.55 | 0.015 | 0.02 | 0.561 | 0.025 | 0.57222
PacifiCorp | 101.7167 | 85 | 87 | 16.7167 | 0.96 | 0 | 0.01 | 0.9792 | 0.02 | 0.99878
Parkland Light & Water Company | 1 | 1 | 1 | 0 | 0.55 | 0.015 | 0.024 | 0.561 | 0.029 | 0.57222
Peninsula Light Company | 2.1845 | 2 | 2 | 0.1845 | 0.55 | 0.015 | 0.02 | 0.561 | 0.025 | 0.57222
Port Angeles City of | 3.7601 | 3 | 3 | 0.76015 | 0.55 | 0.02 | 0.025 | 0.561 | 0.03 | 0.57222
Portland General Electric Company | 104.1609 | 81 | 82 | 23.1609 | 0.77 | 0.025 | 0.03 | 0.7854 | 0.035 | 0.80111
PUD No 1 of Benton County | 9.0557 | 8 | 9 | 1.0557 | 0.55 | 0.015 | 0.02 | 0.561 | 0.025 | 0.57222
PUD No 1 of Chelan County | 8.0418 | 6 | 7 | 2.0418 | 0.55 | 0.02 | 0.025 | 0.561 | 0.03 | 0.57222
PUD No 1 of Clallam County | 3.3674 | 3 | 4 | 0.36742 | 0.55 | 0.015 | 0.02 | 0.561 | 0.025 | 0.57222
PUD No 1 of Clark County | 47 | 40 | 40 | 7 | 0.33 | 0.007 | 0.012 | 0.3366 | 0.017 | 0.34333
PUD No 1 of Cowlitz County | 24.7785 | 22 | 22 | 2.7785 | 0.55 | 0.015 | 0.02 | 0.561 | 0.025 | 0.57222
PUD No 1 of Douglas County | 3.1112 | 3 | 4 | 0.1112 | 0.55 | 0.015 | 0.02 | 0.561 | 0.025 | 0.57222
PUD No 1 of Ferry County | 1 | 1 | 1 | 0 | 0.55 | 0.015 | 0.024 | 0.561 | 0.029 | 0.57222
PUD No 1 of Franklin County | 4.5797 | 4 | 4 | 0.57967 | 0.55 | 0.02 | 0.025 | 0.561 | 0.03 | 0.57222
PUD No 1 of Grays Harbor Cnty | 5.6104 | 5 | 5 | 0.61041 | 0.55 | 0.02 | 0.025 | 0.561 | 0.03 | 0.57222
PUD No 1 of Kittitas County | 1 | 1 | 1 | 0 | 0.55 | 0.015 | 0.024 | 0.561 | 0.029 | 0.57222
PUD No 1 of Klickitat County | 1.595 | 1 | 1 | 0.59497 | 0.55 | 0.015 | 0.02 | 0.561 | 0.025 | 0.57222
PUD No 1 of Lewis County | 4.5675 | 4 | 4 | 0.56754 | 0.55 | 0.015 | 0.02 | 0.561 | 0.025 | 0.57222
PUD No 1 of Mason County | 1 | 1 | 1 | 0 | 0.55 | 0.015 | 0.024 | 0.561 | 0.029 | 0.57222
PUD No 1 of Okanogan County | 1.2233 | 1 | 2 | 0.22335 | 0.55 | 0.015 | 0.02 | 0.561 | 0.025 | 0.57222
PUD No 1 of Pend Oreille Cnty | 5.5215 | 5 | 5 | 0.52147 | 0.55 | 0.015 | 0.02 | 0.561 | 0.025 | 0.57222
PUD No 1 of Skamania Co | 1 | 1 | 1 | 0 | 0.55 | 0.015 | 0.024 | 0.561 | 0.029 | 0.57222
PUD No 1 of Whatcom County | 1.171 | 0 | 0 | 1.171 |  | 0 | 0 |  | 0
PUD No 1 Wahkiakum County | 1 | 1 | 1 | 0 | 0.55 | 0.015 | 0.024 | 0.561 | 0.029 | 0.57222
PUD No 2 of Grant County | 17.0579 | 12 | 17 | 5.0579 | 0.55 | 0.015 | 0.02 | 0.561 | 0.025 | 0.57222
PUD No 3 of Mason County | 3.4937 | 3 | 3 | 0.49372 | 0.55 | 0.02 | 0.025 | 0.561 | 0.03 | 0.57222
Puget Sound Energy Inc | 321 | 272 | 275 | 49 | 0.88 | 0.0239 | 0.0289 | 0.8976 | 0.0339 | 0.91555
Raft River Rural Elec Coop Inc | 1.1255 | 1 | 1 | 0.12553 | 0.55 | 0.015 | 0.024 | 0.561 | 0.029 | 0.57222
Ravalli County Elec Coop, Inc | 1 | 1 | 1 | 0 | 0.55 | 0.015 | 0.024 | 0.561 | 0.029 | 0.57222
Rupert City of | 1 | 1 | 1 | 0 | 0.55 | 0.02 | 0.029 | 0.561 | 0.034 | 0.57222
Salem Electric | 1 | 1 | 1 | 0 | 0.55 | 0.015 | 0.024 | 0.561 | 0.029 | 0.57222
Salmon River Electric Coop Inc | 1.542 | 1 | 1 | 0.54199 | 0.55 | 0.015 | 0.02 | 0.561 | 0.025 | 0.57222
Seattle City of | 14 | 11 | 11 | 3 |  |  | 0 |  | 0
Snohomish County PUD No 1 | 74 | 67 | 67 | 7 | 0.715 | 0.004 | 0.009 | 0.7293 | 0.014 | 0.74389
South Side Electric, Inc | 1 | 1 | 1 | 0 | 0.55 | 0.015 | 0.024 | 0.561 | 0.029 | 0.57222
Surprise Valley Electrification Corp. | 1 | 1 | 1 | 0 | 0.55 | 0.015 | 0.024 | 0.561 | 0.029 | 0.57222
Tacoma City of | 26.1223 | 24 | 24 | 2.1223 | 0.77 | 0.02 | 0.025 | 0.7854 | 0.03 | 0.80111
Tanner Electric Coop | 1 | 1 | 1 | 0 | 0.55 | 0.015 | 0.024 | 0.561 | 0.029 | 0.57222
Tillamook Peoples Utility Dist | 2.2727 | 2 | 2 | 0.27271 | 0.55 | 0.015 | 0.02 | 0.561 | 0.025 | 0.57222
Town of Eatonville | 1 | 1 | 1 | 0 | 0.55 | 0.02 | 0.029 | 0.561 | 0.034 | 0.57222
Town of Ruston | 1 | 1 | 1 | 0 | 0.55 | 0.02 | 0.029 | 0.561 | 0.034 | 0.57222
Town of Steilacoom | 1 | 1 | 1 | 0 | 0.55 | 0.02 | 0.029 | 0.561 | 0.034 | 0.57222
Umatilla Electric Coop Assn | 3.3787 | 3 | 3 | 0.37871 | 0.55 | 0.015 | 0.02 | 0.561 | 0.025 | 0.57222
United Electric Co-op, Inc | 1 | 1 | 1 | 0 | 0.55 | 0.015 | 0.024 | 0.561 | 0.029 | 0.57222
USBIA-Mission Valley Power | 1.1001 | 1 | 1 | 0.10013 | 0.55 | 0.015 | 0.024 | 0.561 | 0.029 | 0.57222
Vera Irrigation District #15 | 1.1361 | 1 | 1 | 0.13605 | 0.55 | 0.015 | 0.024 | 0.561 | 0.029 | 0.57222
Vigilante Electric Coop, Inc | 1 | 1 | 1 | 0 | 0.55 | 0.015 | 0.024 | 0.561 | 0.029 | 0.57222
Wasco Electric Coop, Inc | 1 | 1 | 1 | 0 | 0.55 | 0.015 | 0.024 | 0.561 | 0.029 | 0.57222
Wells Rural Electric Co | 1 | 1 | 1 | 0 | 0.55 | 0.015 | 0.024 | 0.561 | 0.029 | 0.57222
West Oregon Electric Coop Inc | 1 | 1 | 1 | 0 | 0.55 | 0.015 | 0.024 | 0.561 | 0.029 | 0.57222
Total Result | 1362.0778 | 1194 | 1230 | 168.0778 | 71.47 | 2.1185 | 3.0545 | 72.8994 | 3.6945 | 74.3574

## 7P Source Data
UTILITY_NAME | Number of Substations 2005 | No. Subs Res/Comm 2005 | No. Subs Res/Comm in 2012 | Industrial Subs 2005 | ECM1 %dV | ECM1 CVRf | ECM2 %dV | ECM2 CVRf | ECM3 %dV | ECM3 CVRf
Puget Sound Energy Inc | 321 | 272 | 275 | 49 | 0.0239 | 0.88 | 0.0289 | 0.8976 | 0.0339 | 0.91555
Portland General Electric Company | 104.1609 | 81 | 82 | 23.1609 | 0.025 | 0.77 | 0.03 | 0.7854 | 0.035 | 0.80111
PacifiCorp | 76.2875 | 65 | 65 | 11.2875 | 0 | 0.48 | 0.005 | 0.4896 | 0.01 | 0.49939
Avista Corp | 122 | 122 | 122 | 0 | 0.015 | 0.924 | 0.02 | 0.94248 | 0.025 | 0.96133
Idaho Power Co | 209 | 188 | 194 | 21 | 0.0286 | 0.451 | 0.0336 | 0.46002 | 0.0386 | 0.46922
Seattle City of | 14 | 11 | 11 | 3 |  |  | 0 |  | 0
NorthWestern Corporation | 39.664 | 32 | 40 | 7.664 | 0.01 | 0.55 | 0.015 | 0.561 | 0.02 | 0.57222
Snohomish County PUD No 1 | 74 | 67 | 67 | 7 | 0.004 | 0.715 | 0.009 | 0.7293 | 0.014 | 0.74389
Tacoma City of | 26.1223 | 24 | 24 | 2.1223 | 0.02 | 0.77 | 0.025 | 0.7854 | 0.03 | 0.80111
PacifiCorp | 25.4292 | 20 | 22 | 5.4292 | 0 | 0.48 | 0.005 | 0.4896 | 0.01 | 0.49939
PUD No 1 of Cowlitz County | 24.7785 | 22 | 22 | 2.7785 | 0.015 | 0.55 | 0.02 | 0.561 | 0.025 | 0.57222
PUD No 1 of Clark County | 47 | 40 | 40 | 7 | 0.007 | 0.33 | 0.012 | 0.3366 | 0.017 | 0.34333
PUD No 2 of Grant County | 17.0579 | 12 | 17 | 5.0579 | 0.015 | 0.55 | 0.02 | 0.561 | 0.025 | 0.57222
Eugene City of | 34 | 31 | 31 | 3 | 0.02 | 0.77 | 0.025 | 0.7854 | 0.03 | 0.80111
PUD No 1 of Benton County | 9.0557 | 8 | 9 | 1.0557 | 0.015 | 0.55 | 0.02 | 0.561 | 0.025 | 0.57222
PUD No 1 of Chelan County | 8.0418 | 6 | 7 | 2.0418 | 0.02 | 0.55 | 0.025 | 0.561 | 0.03 | 0.57222
Flathead Electric Coop Inc | 7.8003 | 8 | 11 | -0.19968 | 0.01 | 0.55 | 0.015 | 0.561 | 0.02 | 0.57222
Central Lincoln People's Ut Dt | 7.3031 | 7 | 7 | 0.30308 | 0.02 | 0.55 | 0.025 | 0.561 | 0.03 | 0.57222
PUD No 1 of Grays Harbor Cnty | 5.6104 | 5 | 5 | 0.61041 | 0.02 | 0.55 | 0.025 | 0.561 | 0.03 | 0.57222
Clatskanie Peoples Util Dist | 5.5393 | 5 | 1 | 0.53931 | 0.015 | 0.55 | 0.02 | 0.561 | 0.025 | 0.57222
PUD No 1 of Pend Oreille Cnty | 5.5215 | 5 | 5 | 0.52147 | 0.015 | 0.55 | 0.02 | 0.561 | 0.025 | 0.57222
McMinnville City of | 5 | 5 | 5 | 0 | 0.02 | 0.55 | 0.025 | 0.561 | 0.03 | 0.57222
PUD No 1 of Franklin County | 4.5797 | 4 | 4 | 0.57967 | 0.02 | 0.55 | 0.025 | 0.561 | 0.03 | 0.57222
PUD No 1 of Lewis County | 4.5675 | 4 | 4 | 0.56754 | 0.015 | 0.55 | 0.02 | 0.561 | 0.025 | 0.57222
City of Springfield | 4.4259 | 4 | 4 | 0.4259 | 0.02 | 0.55 | 0.025 | 0.561 | 0.03 | 0.57222
City of Richland | 4.2539 | 4 | 4 | 0.25391 | 0.02 | 0.55 | 0.025 | 0.561 | 0.03 | 0.57222
Port Angeles City of | 3.7601 | 3 | 3 | 0.76015 | 0.02 | 0.55 | 0.025 | 0.561 | 0.03 | 0.57222
Idaho Falls City of | 3.6793 | 3 | 3 | 0.67929 | 0.02 | 0.55 | 0.025 | 0.561 | 0.03 | 0.57222
PUD No 3 of Mason County | 3.4937 | 3 | 3 | 0.49372 | 0.02 | 0.55 | 0.025 | 0.561 | 0.03 | 0.57222
Consumers Power, Inc | 3.4876 | 3 | 4 | 0.48757 | 0.015 | 0.55 | 0.02 | 0.561 | 0.025 | 0.57222
Umatilla Electric Coop Assn | 3.3787 | 3 | 3 | 0.37871 | 0.015 | 0.55 | 0.02 | 0.561 | 0.025 | 0.57222
PUD No 1 of Clallam County | 3.3674 | 3 | 4 | 0.36742 | 0.015 | 0.55 | 0.02 | 0.561 | 0.025 | 0.57222
PUD No 1 of Douglas County | 3.1112 | 3 | 4 | 0.1112 | 0.015 | 0.55 | 0.02 | 0.561 | 0.025 | 0.57222
Columbia River Peoples Ut Dist | 7 | 6 | 6 | 1 | 0.015 | 0.55 | 0.02 | 0.561 | 0.025 | 0.57222
Inland Power & Light Company | 2.6729 | 2 | 2 | 0.67289 | 0.015 | 0.55 | 0.02 | 0.561 | 0.025 | 0.57222
Emerald People's Utility Dist | 9 | 8 | 8 | 1 | 0.015 | 0.55 | 0.02 | 0.561 | 0.025 | 0.57222
Big Bend Electric Coop, Inc | 2.2789 | 2 | 6 | 0.27893 | 0.015 | 0.55 | 0.02 | 0.561 | 0.025 | 0.57222
Tillamook Peoples Utility Dist | 2.2727 | 2 | 2 | 0.27271 | 0.015 | 0.55 | 0.02 | 0.561 | 0.025 | 0.57222
Central Electric Coop Inc | 2.2532 | 2 | 2 | 0.25322 | 0.015 | 0.55 | 0.02 | 0.561 | 0.025 | 0.57222
Peninsula Light Company | 2.1845 | 2 | 2 | 0.1845 | 0.015 | 0.55 | 0.02 | 0.561 | 0.025 | 0.57222
Benton Rural Electric Assn | 1.8672 | 2 | 2 | -0.13276 | 0.015 | 0.55 | 0.02 | 0.561 | 0.025 | 0.57222
Lower Valley Energy Inc | 1.8643 | 2 | 2 | -0.13573 | 0.015 | 0.55 | 0.02 | 0.561 | 0.025 | 0.57222
Coos-Curry Electric Coop, Inc | 1.6084 | 1 | 1 | 0.60837 | 0.015 | 0.55 | 0.02 | 0.561 | 0.025 | 0.57222
PUD No 1 of Klickitat County | 1.595 | 1 | 1 | 0.59497 | 0.015 | 0.55 | 0.02 | 0.561 | 0.025 | 0.57222
Pacific Public Utility District No 2 | 1.5882 | 1 | 1 | 0.58824 | 0.015 | 0.55 | 0.02 | 0.561 | 0.025 | 0.57222
Salmon River Electric Coop Inc | 1.542 | 1 | 1 | 0.54199 | 0.015 | 0.55 | 0.02 | 0.561 | 0.025 | 0.57222
Midstate Electric Coop, Inc | 1.4663 | 1 | 1 | 0.46631 | 0.015 | 0.55 | 0.02 | 0.561 | 0.025 | 0.57222
City of Forest Grove | 1.4127 | 1 | 1 | 0.4127 | 0.02 | 0.55 | 0.025 | 0.561 | 0.03 | 0.57222
Oregon Trail El Cons Coop, Inc | 1.3915 | 1 | 2 | 0.39153 | 0.015 | 0.55 | 0.02 | 0.561 | 0.025 | 0.57222
Northern Wasco County PUD | 1.3699 | 1 | 1 | 0.36995 | 0.015 | 0.55 | 0.02 | 0.561 | 0.025 | 0.57222
Kootenai Electric Coop Inc | 1.3172 | 1 | 1 | 0.31719 | 0.015 | 0.55 | 0.02 | 0.561 | 0.025 | 0.57222
City of Centralia | 1.296 | 1 | 1 | 0.29596 | 0.02 | 0.55 | 0.025 | 0.561 | 0.03 | 0.57222
Harney Electric Coop, Inc | 1.2565 | 1 | 1 | 0.25646 | 0.015 | 0.55 | 0.02 | 0.561 | 0.025 | 0.57222
PUD No 1 of Okanogan County | 1.2233 | 1 | 2 | 0.22335 | 0.015 | 0.55 | 0.02 | 0.561 | 0.025 | 0.57222
Elmhurst Mutual Power & Light Co | 1.1941 | 1 | 1 | 0.19405 | 0.015 | 0.55 | 0.02 | 0.561 | 0.025 | 0.57222
PUD No 1 of Whatcom County | 1.171 | 0 | 0 | 1.171 | 0 |  | 0 |  | 0
Lane Electric Coop Inc | 1.1461 | 1 | 1 | 0.14613 | 0.015 | 0.55 | 0.024 | 0.561 | 0.029 | 0.57222
Vera Irrigation District #15 | 1.1361 | 1 | 1 | 0.13605 | 0.015 | 0.55 | 0.024 | 0.561 | 0.029 | 0.57222
Raft River Rural Elec Coop Inc | 1.1255 | 1 | 1 | 0.12553 | 0.015 | 0.55 | 0.024 | 0.561 | 0.029 | 0.57222
Northern Lights, Inc | 1.1165 | 1 | 1 | 0.11647 | 0.015 | 0.55 | 0.024 | 0.561 | 0.029 | 0.57222
USBIA-Mission Valley Power | 1.1001 | 1 | 1 | 0.10013 | 0.015 | 0.55 | 0.024 | 0.561 | 0.029 | 0.57222
Columbia Rural Elec Assn, Inc | 1.0769 | 1 | 1 | 0.076857 | 0.015 | 0.55 | 0.024 | 0.561 | 0.029 | 0.57222
City of Ellensburg | 1.0734 | 1 | 1 | 0.073365 | 0.02 | 0.55 | 0.029 | 0.561 | 0.034 | 0.57222
Salem Electric | 1 | 1 | 1 | 0 | 0.015 | 0.55 | 0.024 | 0.561 | 0.029 | 0.57222
Fall River Rural Elec Coop Inc | 1 | 1 | 2 | 0 | 0.015 | 0.55 | 0.024 | 0.561 | 0.029 | 0.57222
City of Ashland | 1 | 1 | 1 | 0 | 0.02 | 0.55 | 0.029 | 0.561 | 0.034 | 0.57222
Clearwater Power Company | 1 | 1 | 1 | 0 | 0.015 | 0.55 | 0.024 | 0.561 | 0.029 | 0.57222
Canby Utility Board | 1 | 1 | 1 | 0 | 0.02 | 0.55 | 0.029 | 0.561 | 0.034 | 0.57222
Glacier Electric Coop, Inc | 1 | 1 | 1 | 0 | 0.015 | 0.55 | 0.024 | 0.561 | 0.029 | 0.57222
Lakeview Light & Power | 1 | 1 | 1 | 0 | 0.015 | 0.55 | 0.024 | 0.561 | 0.029 | 0.57222
Orcas Power & Light Coop | 5 | 5 | 6 | 0 | 0.015 | 0.55 | 0.024 | 0.561 | 0.029 | 0.57222
Blachly-Lane Cnty Coop El Assn | 1 | 1 | 1 | 0 | 0.015 | 0.55 | 0.024 | 0.561 | 0.029 | 0.57222
Missoula Electric Coop, Inc | 1 | 1 | 1 | 0 | 0.015 | 0.55 | 0.024 | 0.561 | 0.029 | 0.57222
PUD No 1 of Skamania Co | 1 | 1 | 1 | 0 | 0.015 | 0.55 | 0.024 | 0.561 | 0.029 | 0.57222
Douglas Electric Coop, Inc | 1 | 1 | 1 | 0 | 0.015 | 0.55 | 0.024 | 0.561 | 0.029 | 0.57222
Ravalli County Elec Coop, Inc | 1 | 1 | 1 | 0 | 0.015 | 0.55 | 0.024 | 0.561 | 0.029 | 0.57222
City of Cheney | 1 | 1 | 1 | 0 | 0.02 | 0.55 | 0.029 | 0.561 | 0.034 | 0.57222
City of Milton-Freewater | 1 | 1 | 1 | 0 | 0.02 | 0.55 | 0.029 | 0.561 | 0.034 | 0.57222
City of Hermiston | 1 | 1 | 1 | 0 | 0.02 | 0.55 | 0.029 | 0.561 | 0.034 | 0.57222
Lincoln Electric Coop, Inc | 1 | 1 | 1 | 0 | 0.015 | 0.55 | 0.024 | 0.561 | 0.029 | 0.57222
City of Burley | 1 | 1 | 1 | 0 | 0.02 | 0.55 | 0.029 | 0.561 | 0.034 | 0.57222
Columbia Basin Elec Cooperative, Inc | 1 | 1 | 1 | 0 | 0.015 | 0.55 | 0.024 | 0.561 | 0.029 | 0.57222
Modern Electric Water Company | 1 | 1 | 2 | 0 | 0.015 | 0.55 | 0.024 | 0.561 | 0.029 | 0.57222
United Electric Co-op, Inc | 1 | 1 | 1 | 0 | 0.015 | 0.55 | 0.024 | 0.561 | 0.029 | 0.57222
PUD No 1 of Ferry County | 1 | 1 | 1 | 0 | 0.015 | 0.55 | 0.024 | 0.561 | 0.029 | 0.57222
Vigilante Electric Coop, Inc | 1 | 1 | 1 | 0 | 0.015 | 0.55 | 0.024 | 0.561 | 0.029 | 0.57222
Rupert City of | 1 | 1 | 1 | 0 | 0.02 | 0.55 | 0.029 | 0.561 | 0.034 | 0.57222
Wasco Electric Coop, Inc | 1 | 1 | 1 | 0 | 0.015 | 0.55 | 0.024 | 0.561 | 0.029 | 0.57222
City of Bonners Ferry | 1 | 1 | 1 | 0 | 0.02 | 0.55 | 0.029 | 0.561 | 0.034 | 0.57222
Ohop Mutual Light Company, Inc | 1 | 1 | 1 | 0 | 0.015 | 0.55 | 0.024 | 0.561 | 0.029 | 0.57222
City of Blaine | 1 | 1 | 1 | 0 | 0.02 | 0.55 | 0.029 | 0.561 | 0.034 | 0.57222
PUD No 1 of Kittitas County | 1 | 1 | 1 | 0 | 0.015 | 0.55 | 0.024 | 0.561 | 0.029 | 0.57222
PUD No 1 of Mason County | 1 | 1 | 1 | 0 | 0.015 | 0.55 | 0.024 | 0.561 | 0.029 | 0.57222
West Oregon Electric Coop Inc | 1 | 1 | 1 | 0 | 0.015 | 0.55 | 0.024 | 0.561 | 0.029 | 0.57222
City of Bandon | 3 | 3 | 1 | 0 | 0.02 | 0.55 | 0.029 | 0.561 | 0.034 | 0.57222
City of Milton | 1 | 1 | 1 | 0 | 0.02 | 0.55 | 0.029 | 0.561 | 0.034 | 0.57222
City of Weiser | 1 | 1 | 1 | 0 | 0.02 | 0.55 | 0.029 | 0.561 | 0.034 | 0.57222
City of Monmouth | 1 | 1 | 1 | 0 | 0.02 | 0.55 | 0.029 | 0.561 | 0.034 | 0.57222
City of Cashmere | 1 | 1 | 1 | 0 | 0.02 | 0.55 | 0.029 | 0.561 | 0.034 | 0.57222
Parkland Light & Water Company | 1 | 1 | 1 | 0 | 0.015 | 0.55 | 0.024 | 0.561 | 0.029 | 0.57222
Lost River Electric Coop Inc | 1 | 1 | 1 | 0 | 0.015 | 0.55 | 0.024 | 0.561 | 0.029 | 0.57222
Hood River Electric Coop | 1 | 1 | 1 | 0 | 0.015 | 0.55 | 0.024 | 0.561 | 0.029 | 0.57222
Surprise Valley Electrification Corp. | 1 | 1 | 1 | 0 | 0.015 | 0.55 | 0.024 | 0.561 | 0.029 | 0.57222
Wells Rural Electric Co | 1 | 1 | 1 | 0 | 0.015 | 0.55 | 0.024 | 0.561 | 0.029 | 0.57222
Tanner Electric Coop | 1 | 1 | 1 | 0 | 0.015 | 0.55 | 0.024 | 0.561 | 0.029 | 0.57222
City of McCleary | 1 | 1 | 1 | 0 | 0.02 | 0.55 | 0.029 | 0.561 | 0.034 | 0.57222
Nespelem Valley Elec Coop, Inc | 1 | 1 | 1 | 0 | 0.015 | 0.55 | 0.024 | 0.561 | 0.029 | 0.57222
Town of Steilacoom | 1 | 1 | 1 | 0 | 0.02 | 0.55 | 0.029 | 0.561 | 0.034 | 0.57222
Idaho Cnty L&P Coop Assn, Inc | 1 | 1 | 1 | 0 | 0.015 | 0.55 | 0.024 | 0.561 | 0.029 | 0.57222
PUD No 1 Wahkiakum County | 1 | 1 | 1 | 0 | 0.015 | 0.55 | 0.024 | 0.561 | 0.029 | 0.57222
Okanogan County Elec Coop, Inc | 1 | 1 | 1 | 0 | 0.015 | 0.55 | 0.024 | 0.561 | 0.029 | 0.57222
City of Plummer | 1 | 1 | 1 | 0 | 0.02 | 0.55 | 0.029 | 0.561 | 0.034 | 0.57222
Heyburn City of | 1 | 1 | 1 | 0 | 0.02 | 0.55 | 0.029 | 0.561 | 0.034 | 0.57222
City of Sumas | 1 | 1 | 1 | 0 | 0.02 | 0.55 | 0.029 | 0.561 | 0.034 | 0.57222
South Side Electric, Inc | 1 | 1 | 1 | 0 | 0.015 | 0.55 | 0.024 | 0.561 | 0.029 | 0.57222
Town of Eatonville | 1 | 1 | 1 | 0 | 0.02 | 0.55 | 0.029 | 0.561 | 0.034 | 0.57222
Columbia Power Coop Assn Inc | 1 | 1 | 1 | 0 | 0.015 | 0.55 | 0.024 | 0.561 | 0.029 | 0.57222
City of Soda Springs | 1 | 1 | 1 | 0 | 0.02 | 0.55 | 0.029 | 0.561 | 0.034 | 0.57222
City of Chewelah | 1 | 1 | 1 | 0 | 0.02 | 0.55 | 0.029 | 0.561 | 0.034 | 0.57222
City of Drain | 1 | 1 | 1 | 0 | 0.02 | 0.55 | 0.029 | 0.561 | 0.034 | 0.57222
City of Cascade Locks | 1 | 1 | 1 | 0 | 0.02 | 0.55 | 0.029 | 0.561 | 0.034 | 0.57222
City of Coulee Dam | 1 | 1 | 1 | 0 | 0.02 | 0.55 | 0.029 | 0.561 | 0.034 | 0.57222
East End Mutual Elec Co Ltd | 1 | 1 | 1 | 0 | 0.015 | 0.55 | 0.024 | 0.561 | 0.029 | 0.57222
City of Troy | 1 | 1 | 1 | 0 | 0.02 | 0.55 | 0.029 | 0.561 | 0.034 | 0.57222
Town of Ruston | 1 | 1 | 1 | 0 | 0.02 | 0.55 | 0.029 | 0.561 | 0.034 | 0.57222
Alder Mutual Light Co, Inc | 1 | 1 | 1 | 0 | 0.015 | 0.55 | 0.024 | 0.561 | 0.029 | 0.57222
City of Albion | 1 | 1 | 1 | 0 | 0.02 | 0.55 | 0.029 | 0.561 | 0.034 | 0.57222
City of Declo | 1 | 1 | 1 | 0 | 0.02 | 0.55 | 0.029 | 0.561 | 0.034 | 0.57222
Farmers Electric Company, Ltd | 1 | 1 | 1 | 0 | 0.015 | 0.55 | 0.024 | 0.561 | 0.029 | 0.57222
City of Minidoka | 1 | 1 | 1 | 0 | 0.02 | 0.55 | 0.029 | 0.561 | 0.034 | 0.57222
Note on A8: Hadley: "the larger utilities that do not have voltage regulation on the low side of the power transformers were analyzed separately because of the higher capital investment required to install voltage regulation." Page 4-4 of Report.

## 2018 Sales Source Data
2018 Regional Sales Numbers
Source: Massoud Jourabchi, Nov 4, 2019. Modifications: Filtered on the "Region" row and deleted all of those from EMT since they are not in the Plan area. Purpose: Used to create the "20XX Sales" sheets, which are a Pivot Table of the respective "20XX Sales Source Data" sheets. The reason for the pivot table is to sum the sales for states with multiple rows due to either operating in different states (eg Avista in ID, WA, and WMT) or selling both bundled and delivered C&I energy (eg. PGE). Note: The column order between years 2012 and 2018 in these source files are not the same. It does not impact this work since it is the Pivot "20XX Sales" sheets that are used in the System Analysis sheet, but just FYI.
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Mapping | YEAR | UTILITY_ID | UTILITY_NAME | Balancing area | Bundle | Public/IOU | region | State | Owner Type | Res Revenue (000) | Res Sales (MWh) | Res Consumers (n) | Com Revenue (000) | Com Sales (MWh) | Com Consumers (n) | Ind Revenue (000) | Ind Sales (MWh) | Ind Consumers (n) | Trans Rev (000) | Trans Sales (MWh) | Trans Consumers (n) | Total Revenue (000) | Total Sales (MWh) | Total Consumers (n)
City of AlbionID | 2018 | 244 | City of Albion | Bonneville Power Administration | Bundle | Public | ID | ID | Municipal | 189.0709 | 2011.3514 | 176.7826 | 71.9291 | 906.6486 | 37.2174 | 0 | 0 | 0 | 0 | 0 | 0 | 261 | 2918 | 214
Alder Mutual Light Co, IncWA | 2018 | 287 | Alder Mutual Light Co, Inc | Bonneville Power Administration | Bundle | Public | WA | WA | Cooperative | 280.1719 | 4628.0985 | 264.9294 | 28.6281 | 472.9015 | 27.0706 | 0 | 0 | 0 | 0 | 0 | 0 | 308.8 | 5101 | 292
BP Energy CompanyWA | 2018 | 540 | BP Energy Company | Puget Sound Energy | Energy |  | WA | WA | Power Marketer | 0 | 0 | 0 | 0 | 0 | 0 | 21781 | 833304 | 2 | 0 | 0 | 0 | 21781 | 833304 | 2
City of AshlandOR | 2018 | 907 | City of Ashland | PacifiCorp-West | Bundle | public | OR | OR | Municipal | 7964.5 | 86287 | 10395 | 7538.5 | 85629 | 1583 | . | . | . | . | . | . | 15503 | 171916 | 11978
City of BandonOR | 2018 | 1176 | City of Bandon | BPAT | Bundle |  |  | OR | Municipal | 3023.2 | 34708 | 3006 | 1948.2 | 24096 | 769 | 177.9 | 1549 | 2 | 0 | 0 | 0 | 5149.3 | 60353 | 3777
PUD No 1 of Benton CountyWA | 2018 | 1579 | PUD No 1 of Benton County | Bonneville Power Administration | Bundle | Public | WA | WA | Political Subdivision | 59727 | 698135 | 46438 | 37648 | 552107 | 6318 | 26956 | 490607 | 988 | . | . | . | 124331 | 1740849 | 53744
Benton Rural Electric AssnWA | 2018 | 1625 | Benton Rural Electric Assn | Bonneville Power Administration | Bundle | public | WA | WA | Cooperative | 18057 | 208105 | 11660 | 8815 | 130729 | 1393 | 12813 | 206962 | 1371 | . | . | . | 39685 | 545796 | 14424
Big Bend Electric Coop, IncWA | 2018 | 1723 | Big Bend Electric Coop, Inc | Bonneville Power Administration | Bundle | public | WA | WA | Cooperative | 8014 | 103377 | 5016 | 7906 | 106379 | 1866 | 19416 | 328361 | 2467 | 0 | 0 | 0 | 35336 | 538117 | 9349
Blachly-Lane Cnty Coop El AssnOR | 2018 | 1736 | Blachly-Lane Cnty Coop El Assn | Bonneville Power Administration | Bundle | public | OR | OR | Cooperative | 6503.8 | 49387 | 3233 | 946.6 | 10817 | 358 | 6319.7 | 111472 | 25 | . | . | . | 13770.1 | 171676 | 3616
Bonneville Power AdministrationOR | 2018 | 1738 | Bonneville Power Administration | Bonneville Power Administration | Bundle | public | OR | OR | Federal | 0 | 0 | 0 | 223.5 | 5507 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 223.5 | 5507 | 1
Bonneville Power AdministrationWA | 2018 | 1738 | Bonneville Power Administration | Bonneville Power Administration | Bundle | public | WA | WA | Federal | 0 | 0 | 0 | 33359.8 | 776998 | 7 | 43341.2 | 4154734 | 3 | 0 | 0 | 0 | 76701 | 4931732 | 10
City of BlaineWA | 2018 | 1818 | City of Blaine | Puget Sound Energy | Bundle | public | WA | WA | Municipal | 1980 | 26502 | 2856 | 3208 | 38836 | 526 | 936 | 11420 | 13 | . | . | . | 6124 | 76758 | 3395
City of Bonners FerryID | 2018 | 1956 | City of Bonners Ferry | Bonneville Power Administration | Bundle | Public | ID | ID | Municipal | 1731.5725 | 26446.0485 | 2044.2683 | 1663.2618 | 27999.376 | 665.4546 | 1542.1656 | 22944.5755 | 57.277 | 0 | 0 | 0 | 4937 | 77390 | 2767
City of BurleyID | 2018 | 2545 | City of Burley | Bonneville Power Administration | Bundle | public | ID | ID | Municipal | 3322.3 | 46306 | 3986 | 4983.4 | 69459 | 782 | . | . | . | . | . | . | 8305.7 | 115765 | 4768
Canby Utility BoardOR | 2018 | 2955 | Canby Utility Board | Portland General Electric Company | Bundle | Public | OR | OR | Municipal | 6228.7 | 76959 | 6668 | 4304.1 | 72556 | 781 | 2091.8 | 35532 | 13 | 0 | 0 | 0 | 12624.6 | 185047 | 7462
City of Cascade LocksOR | 2018 | 3136 | City of Cascade Locks | Bonneville Power Administration | Bundle | Public | OR | OR | Municipal | 793.2616 | 10091.8732 | 415.084 | 947.7384 | 12057.1268 | 495.916 | 0 | 0 | 0 | 0 | 0 | 0 | 1741 | 22149 | 911
Central Electric Coop IncOR | 2018 | 3240 | Central Electric Coop Inc | Bonneville Power Administration | Bundle | public | OR | OR | Cooperative | 42831 | 491376 | 30048 | 9326 | 121002 | 2832 | 7057 | 108849 | 1628 | . | . | . | 59214 | 721227 | 34508
Central Lincoln People's Ut DtOR | 2018 | 3264 | Central Lincoln People's Ut Dt | Bonneville Power Administration | Bundle | Public | OR | OR | Political Subdivision | 40423 | 415852 | 33807 | 16251 | 191006 | 5192 | 30021 | 689506 | 182 | . | . | . | 86695 | 1296364 | 39181
City of CentraliaWA | 2018 | 3295 | City of Centralia | Bonneville Power Administration | Bundle | public | WA | WA | Municipal | 11280 | 115021 | 8655 | 3803 | 33489 | 1488 | 10747 | 112016 | 139 | . | . | . | 25830 | 260526 | 10282
PUD No 1 of Chelan CountyWA | 2018 | 3413 | PUD No 1 of Chelan County | CHPD | Bundle | Public | WA | WA | Political Subdivision | 26019.1 | 809774 | 38447 | 16883.4 | 486579 | 10508 | 7366 | 338664 | 1501 | . | . | . | 50268.5 | 1635017 | 50456
City of CheneyWA | 2018 | 3420 | City of Cheney | Avista Corp. | Bundle | public | WA | WA | Municipal | 4529.5 | 57860 | 5229 | 3875.6 | 67246 | 438 | 816.3 | 14571 | 9 | 0 | 0 | 0 | 9221.4 | 139677 | 5676
City of ChewelahWA | 2018 | 3459 | City of Chewelah | Avista Corp. | Bundle | Public | WA | WA | Municipal | 836.9524 | 11436.6981 | 1091.2839 | 788.1869 | 10396.9983 | 201.7161 | 0 | 0 | 0 | 0 | 0 | 0 | 1717 | 21475 | 1293
PUD No 1 of Clallam CountyWA | 2018 | 3644 | PUD No 1 of Clallam County | Bonneville Power Administration | Bundle | Public | WA | WA | Political Subdivision | 43870.3 | 439440 | 28527 | 14163.3 | 172619 | 3377 | 1286.1 | 20161 | 1 | . | . | . | 59319.7 | 632220 | 31905
PUD No 1 of Clark CountyWA | 2018 | 3660 | PUD No 1 of Clark County | Bonneville Power Administration | Bundle | Public | WA | WA | Political Subdivision | 219162 | 2364873 | 190404 | 100643 | 1335558 | 18284 | 42480 | 764602 | 29 | . | . | . | 362285 | 4465033 | 208717
Clearwater Power CompanyID | 2018 | 3739 | Clearwater Power Company | Avista Corp. | Bundle | public | ID | ID | Cooperative | 13791.2 | 117662 | 8816 | 2571.1 | 26610 | 769 | 1260 | 22040 | 3 | . | . | . | 17622.3 | 166312 | 9588
Clearwater Power CompanyOR | 2018 | 3739 | Clearwater Power Company | Bonneville Power Administration | Bundle | public | OR | OR | Cooperative | 182.7 | 1449 | 147 | 51.4 | 435 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 234.1 | 1884 | 176
Clearwater Power CompanyWA | 2018 | 3739 | Clearwater Power Company | Avista Corp. | Bundle | public | WA | WA | Cooperative | 1209.5 | 10031 | 854 | 371.9 | 3477 | 135 | 485.7 | 7449 | 1 | 0 | 0 | 0 | 2067.1 | 20957 | 990
Columbia Basin Elec Cooperative, IncOR | 2018 | 4005 | Columbia Basin Elec Cooperative, Inc | Bonneville Power Administration | Bundle | public | OR | OR | Cooperative | 4246.5 | 39961 | 3128 | 2195.9 | 27108 | 518 | 2564.9 | 41891 | 244 | . | . | . | 9007.3 | 108960 | 3890
Columbia Power Coop Assn IncOR | 2018 | 4008 | Columbia Power Coop Assn Inc | Bonneville Power Administration | Bundle | public | OR | OR | Cooperative | 1589 | 13579 | 1401 | 470 | 4549 | 238 | 408 | 5250 | 255 | . | . | . | 2467 | 23378 | 1894
Columbia Rural Elec Assn, IncOR | 2018 | 4041 | Columbia Rural Elec Assn, Inc | Bonneville Power Administration | Bundle | public | OR | OR | Cooperative | 95.8 | 818 | 45 | 100.9 | 333 | 33 | 329.5 | 4044 | 67 | . | . | . | 526.2 | 5195 | 145
Columbia Rural Elec Assn, IncWA | 2018 | 4041 | Columbia Rural Elec Assn, Inc | Bonneville Power Administration | Bundle | public | WA | WA | Cooperative | 6428.8 | 52308 | 3782 | 6883.2 | 72022 | 1509 | 15827.3 | 209144 | 542 | . | . | . | 29139.3 | 333474 | 5833
Coos-Curry Electric Coop, IncOR | 2018 | 4317 | Coos-Curry Electric Coop, Inc | Bonneville Power Administration | Bundle | public | OR | OR | Cooperative | 21889.2 | 179106 | 15286 | 10018.1 | 91608 | 2145 | 4933.1 | 57767 | 447 | . | . | . | 36840.4 | 328481 | 17878
Shell Energy North America (US), L.P.OR | 2018 | 4410 | Shell Energy North America (US), L.P. | Portland General Electric Company | Energy |  | OR | OR | Power Marketer | 0 | 0 | 0 | 912.2 | 28651 | 2 | 4240.5 | 138255 | 4 | 0 | 0 | 0 | 5152.7 | 166906 | 6
Shell Energy North America (US), L.P.WA | 2018 | 4410 | Shell Energy North America (US), L.P. | Puget Sound Energy | Energy |  | WA | WA | Power Marketer | 0 | 0 | 0 | 0 | 0 | 0 | 31575.9 | 1154957 | 4 | 0 | 0 | 0 | 31575.9 | 1154957 | 4
City of Coulee DamWA | 2018 | 4414 | City of Coulee Dam | Bonneville Power Administration | Bundle | Public | WA | WA | Municipal | 518.2112 | 9334.616 | 339.0379 | 394.2888 | 7102.384 | 257.9621 | 0 | 0 | 0 | 0 | 0 | 0 | 912.5 | 16437 | 597
PUD No 1 of Cowlitz CountyWA | 2018 | 4442 | PUD No 1 of Cowlitz County | BPAT | Bundle |  |  | WA | Political Subdivision | 61814 | 711762 | 44591 | 32726 | 382495 | 5848 | 176693 | 3745632 | 312 | 0 | 0 | 0 | 271233 | 4839889 | 50751
Consumers Power, IncOR | 2018 | 4743 | Consumers Power, Inc | Bonneville Power Administration | Bundle | Public | OR | OR | Cooperative | 27685.7 | 273091 | 20373 | 7130.5 | 87933 | 1752 | 2819.1 | 40918 | 530 | . | . | . | 37635.3 | 401942 | 22655
PUD No 1 of Douglas CountyWA | 2018 | 5326 | PUD No 1 of Douglas County | PUD No. 1 of Douglas County | Bundle | Public | WA | WA | Political Subdivision | 12996 | 423075 | 14927 | 10795 | 381532 | 753 | 5648 | 201110 | 75 | . | . | . | 29439 | 1005717 | 15755
Douglas Electric Coop, IncOR | 2018 | 5327 | Douglas Electric Coop, Inc | PUD No. 1 of Douglas County | Bundle | public | OR | OR | Cooperative | 12923 | 125093 | 9335 | 1981 | 18752 | 741 | 770 | 7189 | 11 | . | . | . | 15674 | 151034 | 10087
City of DrainOR | 2018 | 5354 | City of Drain | Bonneville Power Administration | Bundle | Public | OR | OR | Municipal | 699.6381 | 7592.5452 | 357.4135 | 323.7445 | 3513.3088 | 165.3864 | 450.6174 | 4890.146 | 7.1617 | 0 | 0 | 0 | 1474 | 15996 | 753
East End Mutual Elec Co LtdID | 2018 | 5584 | East End Mutual Elec Co Ltd | Bonneville Power Administration | Bundle | Public | ID | ID | Cooperative | 1218.7374 | 15232.1858 | 498 | 693.2626 | 9171.8142 | 249 | 0 | 0 | 0 | 0 | 0 | 0 | 1912 | 24404 | 747
Town of EatonvilleWA | 2018 | 5631 | Town of Eatonville | Bonneville Power Administration | Bundle | Public | WA | WA | Municipal | 1174.7677 | 16229.4389 | 1036.7938 | 920.2323 | 10539.5686 | 195.2337 | 0 | 0 | 0 | 0 | 0 | 0 | 2095 | 26769 | 1231
Elmhurst Mutual Power & Light CoWA | 2018 | 5832 | Elmhurst Mutual Power & Light Co | Bonneville Power Administration | Bundle | Public | WA | WA | Cooperative | 16369 | 229819 | 14793 | 2498 | 41425 | 669 | . | . | . | . | . | . | 18867 | 271244 | 15462
City of EugeneOR | 2018 | 6022 | City of Eugene | Bonneville Power Administration | Bundle | public | OR | OR | Municipal | 103511.9 | 914487 | 83560 | 78198.9 | 869518 | 9371 | 30904.1 | 557949 | 1031 | 0 | 0 | 0 | 212614.9 | 2341954 | 93962
City of EllensburgWA | 2018 | 6149 | City of Ellensburg | Bonneville Power Administration | Bundle | public | WA | WA | Municipal | 7351.4 | 76934 | 8275 | 8425.1 | 120212 | 1498 | 634 | 8136 | 1 | 0 | . | . | 16410.5 | 205282 | 9774
Farmers Electric Company, LtdID | 2018 | 6155 | Farmers Electric Company, Ltd | Bonneville Power Administration | Bundle | Public | ID | ID | Cooperative | 93.4979 | 1801.7107 | 103.6325 | 111.6181 | 1827.7997 | 12.8205 | 0 | 0 | 0 | 0 | 0 | 0 | 214 | 3803 | 125
Fall River Rural Elec Coop IncID | 2018 | 6169 | Fall River Rural Elec Coop Inc | Bonneville Power Administration | Bundle | public | ID | ID | Cooperative | 17211 | 154628 | 12281 | 8870 | 104225 | 2414 | . | . | . | . | . | . | 26081 | 258853 | 14695
Fall River Rural Elec Coop IncMT | 2018 | 6169 | Fall River Rural Elec Coop Inc | Bonneville Power Administration | Bundle | public | WMT | MT | Cooperative | 1956 | 17571 | 1436 | 1996 | 23451 | 528 | . | . | . | . | . | . | 3952 | 41022 | 1964
PUD No 1 of Ferry CountyWA | 2018 | 6297 | PUD No 1 of Ferry County | Bonneville Power Administration | Bundle | Public | WA | WA | Political Subdivision | 3831 | 35666 | 2979 | 1100 | 10165 | 506 | 1699.1 | 20895 | 22 | 0 | 0 | 0 | 6630.1 | 66726 | 3507
Flathead Electric Coop IncMT | 2018 | 6395 | Flathead Electric Coop Inc | Bonneville Power Administration | Bundle | public | WMT | MT | Cooperative | 72009 | 754053 | 55402 | 32782 | 457949 | 11416 | 13104 | 240384 | 93 | . | . | . | 117895 | 1452386 | 66911
City of Forest GroveOR | 2018 | 6582 | City of Forest Grove | Bonneville Power Administration | Bundle | public | OR | OR | Municipal | 9256 | 112058 | 9135 | 1881 | 24199 | 852 | 7131 | 110646 | 139 | . | . | . | 18268 | 246903 | 10126
PUD No 1 of Franklin CountyWA | 2018 | 6716 | PUD No 1 of Franklin County | Bonneville Power Administration | Bundle | Public | WA | WA | Political Subdivision | 34672 | 357358 | 24954 | 28904 | 398435 | 1900 | 18221 | 287041 | 326 | . | . | . | 81797 | 1042834 | 27180
City of DecloID | 2018 | 7084 | City of Declo | Bonneville Power Administration | Bundle | Public | ID | ID | Municipal | 11.4824 | 144.1277 | 78.5452 | 6.9555 | 87.3053 | 47.5787 | 2.5621 | 32.1599 | 17.5262 | 0 | 0 | 0 | 21 | 273 | 130
Glacier Electric Coop, IncMT | 2018 | 7262 | Glacier Electric Coop, Inc | NWMT | Bundle |  |  | MT | Cooperative | 7220.6 | 70883 | 5960 | 6827.5 | 79672 | 1763 | 1514 | 19915 | 5 | 0 | 0 | 0 | 15562.1 | 170470 | 7728
Goldenwest Electric Coop, IncMT | 2018 | 7318 | Goldenwest Electric Coop, Inc | SWPP | Bundle | public |  | MT | Cooperative | [12 empty] | 2596 | 24212 | 805
Grand Electric Coop, IncMT | 2018 | 7484 | Grand Electric Coop, Inc | SWPP | Bundle | public |  | MT | Cooperative | 15.3 | 128 | 14 | . | . | . | . | . | . | . | . | . | 15.3 | 128 | 14
PUD No 1 of Grays Harbor CntyWA | 2018 | 7548 | PUD No 1 of Grays Harbor Cnty | Bonneville Power Administration | Bundle | Public | WA | WA | Political Subdivision | 56009.5 | 466645 | 37336 | 34161.6 | 337185 | 5599 | 9825.3 | 152271 | 18 | . | . | . | 99996.4 | 956101 | 42953
City of HermistonOR | 2018 | 8515 | City of Hermiston | Bonneville Power Administration | Bundle | public | OR | OR | Municipal | 4277.1 | 51860 | 4550 | 4088.7 | 55261 | 816 | . | . | . | . | . | . | 8365.8 | 107121 | 5366
City of HeyburnID | 2018 | 8532 | City of Heyburn | Bonneville Power Administration | Bundle | Public | ID | ID | Municipal | 1783.1522 | 30693.6774 | 1526.8447 | 766.469 | 10571.2641 | 132.6213 | 1255.6789 | 20806.0585 | 4.5341 | 0 | 0 | 0 | 3805.3 | 62071 | 1664
Inland Power & Light CompanyID | 2018 | 8699 | Inland Power & Light Company | Bonneville Power Administration | Bundle | Public | ID | ID | Cooperative | 2291.1 | 28091 | 1688 | 364 | 4165 | 141 | 1.8 | 30 | 3 | . | . | . | 2656.9 | 32286 | 1832
Inland Power & Light CompanyWA | 2018 | 8699 | Inland Power & Light Company | Bonneville Power Administration | Bundle | Public | WA | WA | Cooperative | 51290.1 | 628856 | 36210 | 14302.8 | 163681 | 3146 | 5460.1 | 90680 | 519 | . | . | . | 71053 | 883217 | 39875
Hood River Electric CoopOR | 2018 | 8830 | Hood River Electric Coop | Bonneville Power Administration | Bundle | public | OR | OR | Cooperative | 4363 | 52252 | 3406 | 522.9 | 6434 | 245 | 3815.9 | 59703 | 214 | . | . | . | 8701.8 | 118389 | 3865
Idaho Cnty L&P Coop Assn, IncID | 2018 | 9186 | Idaho Cnty L&P Coop Assn, Inc | Avista Corp. | Bundle | public | ID | ID | Cooperative | 4810.4801 | 42956.7001 | 3320.6332 | 965.014 | 8617.3969 | 666.1409 | 23.5059 | 209.903 | 16.2259 | 0 | 0 | 0 | 5799 | 51784 | 4003
Idaho Falls City ofID | 2018 | 9187 | Idaho Falls City of | PacifiCorp-East | Bundle | Public | ID | ID | Municipal | 22300 | 282284 | 23995 | 21899 | 334872 | 4176 | 3435 | 67657 | 4 | 0 | 0 | 0 | 47634 | 684813 | 28175
Idaho Power CoID | 2018 | 9191 | Idaho Power Co | Idaho Power Company | Bundle | IOU | ID | ID | Investor Owned | 515102 | 4957731 | 445693 | 298904.1 | 3953274 | 67607 | 324740.6 | 4996987 | 19101 | 0 | 0 | 0 | 1138746.7 | 13907992 | 532401
Idaho Power CoOR | 2018 | 9191 | Idaho Power Co | Idaho Power Company | Bundle | IOU | OR | OR | Investor Owned | 17960 | 176845 | 13435 | 12897.7 | 151667 | 3497 | 24867.1 | 350018 | 2122 | 0 | 0 | 0 | 55724.8 | 678530 | 19054
PUD No 1 of Kittitas CountyWA | 2018 | 10326 | PUD No 1 of Kittitas County | Bonneville Power Administration | Bundle | Public | WA | WA | Political Subdivision | 5928.7624 | 59494.851 | 2725.5534 | 3108.2978 | 31191.6214 | 1428.9376 | 718.9399 | 7214.5276 | 330.5089 | 0 | 0 | 0 | 9756 | 97901 | 4485
PUD No 1 of Klickitat CountyWA | 2018 | 10393 | PUD No 1 of Klickitat County | Bonneville Power Administration | Bundle | Public | WA | WA | Political Subdivision | 15989 | 141628 | 10522 | 9976 | 111719 | 1937 | 5157 | 91160 | 251 | . | . | . | 31122 | 344507 | 12710
Kootenai Electric Coop IncID | 2018 | 10454 | Kootenai Electric Coop Inc | Avista Corp. | Bundle | Public | ID | ID | Cooperative | 31904.9 | 319600 | 23653 | 10299.6 | 112143 | 1775 | 1804.1 | 30221 | 44 | 0 | 0 | 0 | 44008.6 | 461964 | 25472
Kootenai Electric Coop IncWA | 2018 | 10454 | Kootenai Electric Coop Inc | Avista Corp. | Bundle | Public | WA | WA | Cooperative | 203 | 2323 | 74 | 35.1 | 458 | 1 | 0.2 | 0 | 1 | 0 | 0 | 0 | 238.3 | 2781 | 76
Lakeview Light & PowerWA | 2018 | 10627 | Lakeview Light & Power | Bonneville Power Administration | Bundle | public | WA | WA | Cooperative | 9941 | 106703 | 7922 | 8345.9 | 89895 | 2122 | 4933 | 60571 | 53 | . | . | . | 23219.9 | 257169 | 10097
Lane Electric Coop IncOR | 2018 | 10681 | Lane Electric Coop Inc | Bonneville Power Administration | Bundle | public | OR | OR | Cooperative | 20947.3 | 185955 | 11845 | 4048.4 | 41125 | 1004 | 356.5 | 4356 | 1 | . | . | . | 25352.2 | 231436 | 12850
PUD No 1 of Lewis CountyWA | 2018 | 10944 | PUD No 1 of Lewis County | Bonneville Power Administration | Bundle | Public | WA | WA | Political Subdivision | 37722.8 | 437275 | 26814 | 15845.3 | 218423 | 5384 | 15391.8 | 266679 | 187 | . | . | . | 68959.9 | 922377 | 32385
Lincoln Electric Coop, IncMT | 2018 | 11022 | Lincoln Electric Coop, Inc | Bonneville Power Administration | Bundle | public | WMT | MT | Cooperative | 8153 | 81687 | 5215 | 2372 | 29465 | 670 | 585 | 6803 | 2 | . | . | . | 11110 | 117955 | 5887
Lost River Electric Coop IncID | 2018 | 11211 | Lost River Electric Coop Inc | PacifiCorp-East | Bundle | Public | ID | ID | Cooperative | 2354.8598 | 27149.6098 | 1839.0648 | 450.676 | 5660.9651 | 236.8027 | 0 | 0 | 0 | 0 | 0 | 0 | 5981 | 73841 | 2728
Lower Valley Energy IncID | 2018 | 11273 | Lower Valley Energy Inc | Bonneville Power Administration | Bundle | Public | ID | ID | Cooperative | 1110.6 | 16674 | 1347 | 261.1 | 3822 | 354 | 2409.8 | 51105 | 40 | . | . | . | 3781.5 | 71601 | 1741
Harney Electric Coop, IncOR | 2018 | 11589 | Harney Electric Coop, Inc | Bonneville Power Administration | Bundle | public | OR | OR | Cooperative | 1546.9 | 18799 | 903 | . | . | . | 5200.9 | 82746 | 1445 | . | . | . | 6747.8 | 101545 | 2348
City of McClearyWA | 2018 | 11965 | City of McCleary | Bonneville Power Administration | Bundle | Public | WA | WA | Municipal | 1415.5 | 16771.8821 | 590.1433 | 389.5171 | 4615.2841 | 162.3955 | 878.9829 | 10414.8338 | 366.4612 | 0 | 0 | 0 | 2684 | 31802 | 1119
McCone Electric Coop IncMT | 2018 | 11989 | McCone Electric Coop Inc | WAUW | Bundle |  |  | MT | Cooperative | 6880.1 | 51060 | 4603 | 2584.2 | 22501 | 605 | 221.7 | 1665 | 81 | 0 | 0 | 0 | 9686 | 75226 | 5289
McMinnville City ofOR | 2018 | 12187 | McMinnville City of | Bonneville Power Administration | Bundle | public | OR | OR | Municipal | 13128 | 190078 | 13847 | 12234 | 174545 | 2517 | 15638 | 332565 | 52 | 0 | 0 | 0 | 41000 | 697188 | 16416
Midstate Electric Coop, IncOR | 2018 | 12439 | Midstate Electric Coop, Inc | Bonneville Power Administration | Bundle | public | OR | OR | Cooperative | 23428 | 258677 | 17197 | 8722 | 117183 | 2162 | 2037 | 28415 | 3 | 0 | 0 | 0 | 34187 | 404275 | 19362
City of MinidokaID | 2018 | 12609 | City of Minidoka | Bonneville Power Administration | Bundle | Public | ID | ID | Municipal | 53.4087 | 773.473 | 42.9177 | 2 | 37.527 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 56 | 811 | 45
City of Milton-FreewaterOR | 2018 | 12615 | City of Milton-Freewater | Bonneville Power Administration | Bundle | public | OR | OR | Municipal | 4239 | 58599 | 3551 | 1006 | 14301 | 490 | 2065 | 30992 | 367 | . | . | . | 7310 | 103892 | 4408
City of MiltonWA | 2018 | 12616 | City of Milton | Bonneville Power Administration | Bundle | Public | WA | WA | Municipal | 3085.3622 | 23109.7535 | 2459.438 | 1320.4378 | 9890.2465 | 1052.562 | 0 | 0 | 0 | 0 | 0 | 0 | 4405.8 | 33000 | 3512
Missoula Electric Coop, IncID | 2018 | 12692 | Missoula Electric Coop, Inc | Bonneville Power Administration | Bundle | public | ID | ID | Cooperative | 55.1 | 537 | 37 | 83.7 | 900 | 20 | . | . | . | . | . | . | 138.8 | 1437 | 57
Missoula Electric Coop, IncMT | 2018 | 12692 | Missoula Electric Coop, Inc | Bonneville Power Administration | Bundle | public | MT | MT | Cooperative | 16539.4 | 164445 | 13365 | 4166.6 | 45687 | 1385 | 1527.8 | 17613 | 277 | . | . | . | 22233.8 | 227745 | 15027
Modern Electric Water CompanyWA | 2018 | 12744 | Modern Electric Water Company | Avista Corp. | Bundle | public | WA | WA | Cooperative | 5714.5 | 96035 | 8358 | 7843.3 | 126651 | 1662 | . | . | . | . | . | . | 13557.8 | 222686 | 10020
City of MonmouthOR | 2018 | 12789 | City of Monmouth | Bonneville Power Administration | Bundle | public | OR | OR | Municipal | 3661.5 | 44181 | 4260 | 2076.3 | 27773 | 336 | . | . | . | . | . | . | 5737.8 | 71954 | 4596
NorthWestern CorporationMT | 2018 | 12825 | NorthWestern Corporation | NorthWestern Energy | Bundle | IOU | WMT | MT | Investor Owned | 88844.3057 | 757198.6014 | 90045.8295 | 104389.4918 | 922708.3455 | 21306.1272 | 11526.3055 | 131189.0901 | 529.8849 |  |  |  | 204760.103 | 1811096.037 | 111881.8416
NorthWestern CorporationMT | 2018 | 12825 | NorthWestern Corporation | NorthWestern Energy | Delivery | IOU | WMT | MT | Investor Owned | 0.09027 | 1.8054 | 0.6018 | 1030.5825 | 42951.6696 | 122.4663 | 4269.5303 | 870633.6888 | 11.4342 |  |  |  | 5300.2031 | 913587.1638 | 134.5023
NorthWestern CorporationMT | 2018 | 12825 | NorthWestern Corporation | NorthWestern Energy | Energy | IOU | WMT | MT | Investor Owned | 0 | 0 | 0 | 8462.5116 | 312333.2973 | 0.6018 | 0 | 0 | 0 |  |  |  | 8462.5116 | 312333.2973 | 0.6018
Constellation NewEnergy, IncOR | 2018 | 13374 | Constellation NewEnergy, Inc | PacifiCorp-West | Energy |  | OR | OR | Power Marketer | 0 | 0 | 0 | 5871.4 | 188845 | 97 | 6551.4 | 219980 | 14 | 0 | 0 | 0 | 12422.8 | 408825 | 111
Nespelem Valley Elec Coop, IncWA | 2018 | 13387 | Nespelem Valley Elec Coop, Inc | Bonneville Power Administration | Bundle | Public | WA | WA | Cooperative | 1650.2074 | 17713.296 | 1134.8936 | 1573.4608 | 23299.5732 | 102.3431 | 1605.9104 | 19747.8215 | 279.6702 | 0 | 0 | 0 | 4972.2 | 60886 | 1524
Northern Lights, IncID | 2018 | 13758 | Northern Lights, Inc | Bonneville Power Administration | Bundle | Public | ID | ID | Cooperative | 20621 | 187830 | 14939 | 4385 | 40553 | 882 | 1271 | 23819 | 4 | 0 | 0 | 0 | 26277 | 252202 | 15825
Northern Lights, IncMT | 2018 | 13758 | Northern Lights, Inc | Bonneville Power Administration | Bundle | Public | WMT | MT | Cooperative | 6421 | 44076 | 4017 | 841 | 7296 | 299 | 434 | 4308 | 6 | 0 | 0 | 0 | 7696 | 55680 | 4322
Northern Lights, IncWA | 2018 | 13758 | Northern Lights, Inc | Bonneville Power Administration | Bundle | Public | WA | WA | Cooperative | 15 | 115 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 115 | 15
Northern Wasco County PUDOR | 2018 | 13788 | Northern Wasco County PUD | Bonneville Power Administration | Bundle | Public | OR | OR | Political Subdivision | 10019 | 138890 | 9428 | 1697 | 19690 | 461 | 32378 | 625830 | 223 | . | . | . | 44094 | 784410 | 10112
Ohop Mutual Light Company, IncWA | 2018 | 14012 | Ohop Mutual Light Company, Inc | Bonneville Power Administration | Bundle | public | WA | WA | Cooperative | 6734 | 77776 | 4275 | 345 | 4358 | 126 | 6 | 45 | 12 | . | . | . | 7085 | 82179 | 4413
PUD No 1 of Okanogan CountyWA | 2018 | 14055 | PUD No 1 of Okanogan County | PUD No. 1 of Douglas County | Bundle | Public | WA | WA | Political Subdivision | 23036.2 | 290654 | 17236 | 20613 | 293747 | 3875 | 930.7 | 14993 | 3 | . | . | . | 44579.9 | 599394 | 21114
Okanogan County Elec Coop, IncWA | 2018 | 14074 | Okanogan County Elec Coop, Inc | Bonneville Power Administration | Bundle | Public | WA | WA | Cooperative | 4096.4 | 38314 | 3171 | 1460.6 | 19706 | 403 | . | . | . | . | . | . | 5557 | 58020 | 3574
Oregon Trail El Cons Coop, IncOR | 2018 | 14109 | Oregon Trail El Cons Coop, Inc | Bonneville Power Administration | Bundle | Public | OR | OR | Cooperative | 28485 | 289676 | 25596 | 19665 | 250128 | 5649 | 6708 | 117674 | 9 | . | . | . | 54858 | 657478 | 31254
Orcas Power & Light CoopWA | 2018 | 14170 | Orcas Power & Light Coop | Bonneville Power Administration | Bundle | Public | WA | WA | Cooperative | 21262 | 149472 | 13188 | 7766 | 59261 | 1894 | . | . | . | . | . | . | 29028 | 208733 | 15082
Pacific Public Utility District No 2WA | 2018 | 14324 | Pacific Public Utility District No 2 | Bonneville Power Administration | Bundle | Public | WA | WA | Political Subdivision | 15223.2 | 178573 | 15448 | 7794 | 89854 | 2047 | 1192 | 23011 | 1 | . | . | . | 24209.2 | 291438 | 17496
Avangrid RenewablesOR | 2018 | 14349 | Avangrid Renewables | PacifiCorp-West | Energy |  |  | OR | Power Marketer | . | . | . | 11442.4 | 355456 | 2 | . | . | . | . | . | . | 11442.4 | 355456 | 2
Avangrid RenewablesWA | 2018 | 14349 | Avangrid Renewables | Puget Sound Energy | Energy |  |  | WA | Power Marketer | . | . | . | 954.8 | 32865 | 1 | . | . | . | . | . | . | 954.8 | 32865 | 1
PacifiCorpID | 2018 | 14354 | PacifiCorp | PacifiCorp-East | Bundle | IOU | ID | ID | Investor Owned | 72892.7 | 703239 | 64774 | 45710 | 513764 | 9082 | 168969.7 | 2426431 | 5629 | 0 | 0 | 0 | 287572.4 | 3643434 | 79485
PacifiCorpOR | 2018 | 14354 | PacifiCorp | PacifiCorp-West | Bundle | IOU | OR | OR | Investor Owned | 618755.2 | 5556224 | 509553 | 489388.3 | 5286661 | 68578 | 157916.9 | 2009300 | 9233 | 1471.4 | 15048 | 1 | 1267531.8 | 12867233 | 587365
PacifiCorpOR | 2018 | 14354 | PacifiCorp | PacifiCorp-West | Delivery | IOU | OR | OR | Investor Owned | 0 | 0 | 0 | 10848.2 | 318559 | 25 | 2697.2 | 74462 | 4 | 0 | 0 | 0 | 13545.4 | 393021 | 29
PacifiCorpWA | 2018 | 14354 | PacifiCorp | PacifiCorp-West | Bundle | IOU | WA | WA | Investor Owned | 132837.1 | 1520347 | 109499 | 135585.8 | 1576270 | 16422 | 63214.9 | 852499 | 5532 | 0 | 0 | 0 | 331637.8 | 3949116 | 131453
Parkland Light & Water CompanyWA | 2018 | 14505 | Parkland Light & Water Company | Bonneville Power Administration | Bundle | public | WA | WA | Cooperative | 4255 | 54913 | 3802 | 3941 | 58482 | 764 | . | . | . | . | . | . | 8196 | 113395 | 4566
PUD No 2 of Grant CountyWA | 2018 | 14624 | PUD No 2 of Grant County | PUD No. 2 of Grant County | Bundle | Public | WA | WA | Political Subdivision | 43161 | 765978 | 38368 | 40043 | 961590 | 7137 | 118188 | 3183187 | 5183 | . | . | . | 201392 | 4910755 | 50688
PUD No 1 of Pend Oreille CntyWA | 2018 | 14653 | PUD No 1 of Pend Oreille Cnty | Avista Corp. | Bundle | Public | WA | WA | Political Subdivision | 10312.5 | 145245 | 8382 | 2934.6 | 52432 | 920 | 33766.6 | 802274 | 8 | . | . | . | 47013.7 | 999951 | 9310
Peninsula Light CompanyWA | 2018 | 14668 | Peninsula Light Company | Bonneville Power Administration | Bundle | Public | WA | WA | Cooperative | 48052.2 | 481481 | 33138 | 7841.6 | 99867 | 197 | . | . | . | . | . | . | 55893.8 | 581348 | 33335
PUD No 1 of Asotin CountyWA | 2018 | 14771 | PUD No 1 of Asotin County | Bonneville Power Administration | Bundle | Public | WA | WA | Municipal | 0 | 0 | 0 | 12.3332 | 0.22469 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 13.8 | 247 | 3
Port Angeles City ofWA | 2018 | 15231 | Port Angeles City of | Bonneville Power Administration | Bundle | public | WA | WA | Municipal | 12025 | 123274 | 9093 | 8505 | 101550 | 1872 | 2206 | 44069 | 6 | . | . | . | 22736 | 268893 | 10971
Portland General Electric CompanyOR | 2018 | 15248 | Portland General Electric Company | Portland General Electric Company | Bundle | IOU | OR | OR | Investor Owned | 890376.6 | 7415759 | 776747 | 630655.3 | 6728483 | 107281 | 195560.7 | 3030812 | 3508 | 909.1 | 10948 | 1 | 1717501.7 | 17186002 | 887537
Portland General Electric CompanyOR | 2018 | 15248 | Portland General Electric Company | Portland General Electric Company | Delivery | IOU | OR | OR | Investor Owned | . | . | . | 18220.6 | 646936 | 527 | 24428.6 | 1388558 | 59 | . | . | . | 42649.2 | 2035494 | 586
City of PlummerID | 2018 | 15297 | City of Plummer | Avista Corp. | Bundle | Public | ID | ID | Municipal | 737.8214 | 10182.5212 | 296.7309 | 638.334 | 8809.5158 | 256.7198 | 1018.3446 | 14053.963 | 409.5493 | 0 | 0 | 0 | 2394.5 | 33046 | 963
PUD No 1 of Wahkiakum CountyWA | 2018 | 15327 | PUD No 1 of Wahkiakum County | Bonneville Power Administration | Bundle | Public | WA | WA | Political Subdivision | 2740.8119 | 29739.8738 | 2016.9336 | 1114.521 | 11304.1262 | 508.627 | 0 | 0 | 0 | 0 | 0 | 0 | 3894 | 41044 | 2539
PUD No 3 of Mason CountyWA | 2018 | 15419 | PUD No 3 of Mason County | Bonneville Power Administration | Bundle | Public | WA | WA | Political Subdivision | 45335 | 421592 | 31477 | 16892 | 186277 | 2363 | 2539 | 37814 | 1 | 0 | 0 | 0 | 64766 | 645683 | 33841
Puget Sound Energy IncWA | 2018 | 15500 | Puget Sound Energy Inc | Puget Sound Energy | Bundle | IOU | WA | WA | Investor Owned | 1147260 | 10497389 | 1010574 | 903283.9 | 9004114 | 135828 | 110606.6 | 1189828 | 3362 | 551.4 | 5865 | 1 | 2161701.9 | 20697196 | 1149765
Puget Sound Energy IncWA | 2018 | 15500 | Puget Sound Energy Inc | Puget Sound Energy | Delivery | IOU | WA | WA | Investor Owned | . | . | . | 243.5 | 34644 | 1 | 13634.1 | 1994083 | 15 | . | . | . | 13877.6 | 2028727 | 16
City of RichlandWA | 2018 | 15979 | City of Richland | Bonneville Power Administration | Bundle | public | WA | WA | Municipal | 31249 | 338631 | 23009 | 26927 | 435831 | 1473 | 8805 | 157422 | 45 | . | . | . | 66981 | 931884 | 24527
Rupert City ofID | 2018 | 16416 | Rupert City of | Bonneville Power Administration | Bundle | Public |  | ID | Municipal | 2768.3 | 35718 | 2527 | 1825.5 | 28569 | 438 | 734.8 | 13131 | 47 | 0 | 0 | 0 | 5328.6 | 77418 | 3012
Town of RustonWA | 2018 | 16462 | Town of Ruston | Tacoma Power | Bundle | Public | WA | WA | Municipal | 817.8 | 7475 | 547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 817.8 | 7475 | 547
Salem ElectricOR | 2018 | 16555 | Salem Electric | Bonneville Power Administration | Bundle | Public | OR | OR | Cooperative | 17098.2 | 182733 | 17495 | 9161.2 | 108802 | 2317 | 2035.9 | 26211 | 10 | . | . | . | 28295.3 | 317746 | 19822
Salmon River Electric Coop IncID | 2018 | 16565 | Salmon River Electric Coop Inc | Idaho Power Company | Bundle | public | ID | ID | Cooperative | 2931 | 31663 | 2222 | 1575 | 21865 | 453 | 2336 | 44563 | 122 | . | . | . | 6842 | 98091 | 2797
Calpine Energy Solutions, LLCOR | 2018 | 16840 | Calpine Energy Solutions, LLC | PacifiCorp-West | Energy |  | OR | OR | Power Marketer | 0 | 0 | 0 | 6381.8 | 143969 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 6381.8 | 143969 | 6
Calpine Energy Solutions, LLCOR | 2018 | 16840 | Calpine Energy Solutions, LLC | Portland General Electric Company | Energy |  | OR | OR | Power Marketer | 0 | 0 | 0 | 38334.7 | 1048021 | 29 | 11074 | 280670 | 4 | 0 | 0 | 0 | 49408.7 | 1328691 | 33
Calpine Energy Solutions, LLCWA | 2018 | 16840 | Calpine Energy Solutions, LLC | Puget Sound Energy | Energy |  | WA | WA | Power Marketer | 0 | 0 | 0 | 272.3 | 10223 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 272.3 | 10223 | 1
Seattle City ofWA | 2018 | 16868 | Seattle City of | Seattle Department of Lighting | Bundle | public | WA | WA | Municipal | 321534 | 3000403 | 410664 | 463819 | 5021154 | 50653 | 83187 | 1051774 | 202 | 71 | 730 | 4 | 868611 | 9074061 | 461523
PUD No 1 of Skamania CoWA | 2018 | 17279 | PUD No 1 of Skamania Co | Bonneville Power Administration | Bundle | Public | WA | WA | Political Subdivision | 7265.9 | 75435 | 5487 | 2510 | 28718 | 610 | 1237.1 | 16411 | 4 | 0 | 0 | 0 | 11013 | 120564 | 6101
Snohomish County PUD No 1WA | 2018 | 17470 | Snohomish County PUD No 1 | Bonneville Power Administration | Bundle | Public | WA | WA | Political Subdivision | 362924 | 3566730 | 318471 | 211423 | 2386767 | 31916 | 36727 | 528243 | 80 | 0 | 0 | 0 | 611074 | 6481740 | 350467
City of Soda SpringsID | 2018 | 17493 | City of Soda Springs | PacifiCorp-East | Bundle | Public | ID | ID | Municipal | 1090.2947 | 11797.9554 | 1446.6839 | 1102.6563 | 13965.6271 | 355.2673 | 43.2657 | 397.5642 | 2.2274 | 0 | 0 | 0 | 2271.2 | 26496 | 1871
South Side Electric, IncID | 2018 | 17576 | South Side Electric, Inc | Bonneville Power Administration | Bundle | Public | ID | ID | Cooperative | 1530.7369 | 24232.3489 | 997.1145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3131 | 58794 | 813
City of SpringfieldOR | 2018 | 17839 | City of Springfield | Bonneville Power Administration | Bundle | public | OR | OR | Municipal | 25127 | 370238 | 28341 | 17239 | 256249 | 3924 | 8386 | 139450 | 11 | . | . | . | 50752 | 765937 | 32276
Town of SteilacoomWA | 2018 | 18051 | Town of Steilacoom | Bonneville Power Administration | Bundle | public | WA | WA | Municipal | 2551.8 | 30709 | 2842 | 468.7 | 6306 | 121 | . | . | . | . | . | . | 3020.5 | 37015 | 2963
Surprise Valley Electrification Corp.OR | 2018 | 18260 | Surprise Valley Electrification Corp. | PacifiCorp-West | Bundle | public | OR | OR | Cooperative | 1511.7 | 16127 | 1174 | 446.2 | 4490 | 428 | 1379.8 | 16424 | 312 | 0 | 0 | 0 | 3337.7 | 37041 | 1914
City of SumasWA | 2018 | 18282 | City of Sumas | Puget Sound Energy | Bundle | Public | WA | WA | Municipal | 447.1993 | 6144.1537 | 168.2254 | 391.4206 | 5377.8004 | 147.2429 | 1553.8801 | 21349.0459 | 584.5317 | 0 | 0 | 0 | 2392.5 | 32871 | 900
Tacoma City ofWA | 2018 | 18429 | Tacoma City of | Tacoma Power | Bundle | public | WA | WA | Municipal | 175995.2 | 1863660 | 158427 | 29770.8 | 328887 | 16752 | 148853.5 | 2424144 | 2545 | 47.4 | 542 | 1 | 354666.9 | 4617233 | 177725
Tanner Electric CoopWA | 2018 | 18448 | Tanner Electric Coop | Puget Sound Energy | Bundle | public | WA | WA | Cooperative | 7736 | 58091 | 4610 | 3074 | 32589 | 301 | . | . | . | . | . | . | 10810 | 90680 | 4911
Tillamook Peoples Utility DistOR | 2018 | 18917 | Tillamook Peoples Utility Dist | Bonneville Power Administration | Bundle | Public | OR | OR | Political Subdivision | 22072 | 232930 | 18986 | 10088 | 127363 | 2250 | 5717 | 109595 | 6 | . | . | . | 37877 | 469888 | 21242
Tenaska Power Services CoMT | 2018 | 18995 | Tenaska Power Services Co | NorthWestern Energy | Energy |  | MT | MT | Power Marketer | 0 | 0 | 0 | 0 | 0 | 0 | 14953.3 | 478403 | 3 | 0 | 0 | 0 | 14953.3 | 478403 | 3
Tongue River Electric Coop IncMT | 2018 | 19022 | Tongue River Electric Coop Inc | NorthWestern Energy | Bundle | public |  | MT | Cooperative | 7979 | 56751 | 4293 | 1615 | 12952 | 585 | 3382 | 29557 | 148 | . | . | . | 12976 | 99260 | 5026
City of TroyMT | 2018 | 19236 | City of Troy | Bonneville Power Administration | Bundle | Public | WMT | MT | Municipal | 775.7189 | 11318.4437 | 676.1614 | 341.9453 | 4989.2931 | 298.0593 | 4.3358 | 63.2632 | 3.7793 | 0 | 0 | 0 | 1122 | 16371 | 978
Umatilla Electric Coop AssnOR | 2018 | 19325 | Umatilla Electric Coop Assn | Bonneville Power Administration | Bundle | Public | OR | OR | Cooperative | 13907.8 | 166846 | 11515 | 13168.6 | 210511 | 2269 | 98167.9 | 2155160 | 1504 | . | . | . | 125244.3 | 2532517 | 15288
United Electric Co-op, IncID | 2018 | 19502 | United Electric Co-op, Inc | Bonneville Power Administration | Bundle | Public | ID | ID | Cooperative | 6170.9 | 89525 | 4549 | 3737.2 | 63886 | 1058 | 7436.4 | 144902 | 1129 | . | . | . | 17344.5 | 298313 | 6736
USBIA-Mission Valley PowerMT | 2018 | 19603 | USBIA-Mission Valley Power | NorthWestern Energy | Bundle | public | WMT | MT | Federal | 16052 | 235022 | 15017 | 7775 | 127147 | 5397 | 933 | 18016 | 1048 | 0 | 0 | 0 | 24760 | 380185 | 21462
Vera Irrigation District #15WA | 2018 | 19784 | Vera Irrigation District #15 | Bonneville Power Administration | Bundle | Public | WA | WA | Political Subdivision | 11170 | 142882 | 10677 | 6251 | 78028 | 1220 | . | . | . | . | . | . | 17421 | 220910 | 11897
Wasco Electric Coop, IncOR | 2018 | 20138 | Wasco Electric Coop, Inc | Bonneville Power Administration | Bundle | public | OR | OR | Cooperative | 5823 | 49822 | 3798 | 1923 | 17192 | 563 | 3391 | 39690 | 343 | . | . | . | 11137 | 106704 | 4704
Avista CorpID | 2018 | 20169 | Avista Corp | Avista Corp. | Bundle | IOU | ID | ID | Investor Owned | 120586 | 1182924 | 115122 | 95105 | 1009257 | 17860 | 45129 | 786238 | 419 | 0 | 0 | 0 | 260820 | 2978419 | 133401
Avista CorpWA | 2018 | 20169 | Avista Corp | Avista Corp. | Bundle | IOU | WA | WA | Investor Owned | 248149 | 2443747 | 227866 | 228271 | 2178273 | 25488 | 64718 | 986043 | 878 | 0 | . | . | 541138 | 5608063 | 254232
Avista CorpMT | 2018 | 20169 | Avista Corp | Avista Corp. | Bundle | IOU | WMT | MT | Investor Owned | 18 | 200 | 8 | 80 | 858 | 21 | 0 | . | . | 0 | . | . | 98 | 1058 | 29
City of WeiserID | 2018 | 20297 | City of Weiser | Bonneville Power Administration | Bundle | Public | ID | ID | Municipal | 1590.0972 | 24693.4239 | 1780.5815 | 898.1573 | 13947.9396 | 1005.7513 | 621.2455 | 9647.6365 | 1.2877 | 0 | 0 | 0 | 3109.5 | 48289 | 3482
West Oregon Electric Coop IncOR | 2018 | 20385 | West Oregon Electric Coop Inc | Bonneville Power Administration | Bundle | Public | OR | OR | Cooperative | 8968.0626 | 50619.7344 | 3435.7994 | 893.7543 | 5044.7466 | 342.4107 | 1596.8832 | 9013.519 | 611.7899 | 0 | 0 | 0 | 11458.7 | 64678 | 4390
PUD No 1 of Mason CountyWA | 2018 | 22355 | PUD No 1 of Mason County | Bonneville Power Administration | Bundle | Public | WA | WA | Political Subdivision | 6722.5462 | 59641.3137 | 4172.4246 | 1805.4538 | 16017.6863 | 1120.5754 | 0 | 0 | 0 | 0 | 0 | 0 | 8528 | 75659 | 5293
Raft River Rural Elec Coop IncID | 2018 | 22814 | Raft River Rural Elec Coop Inc | Bonneville Power Administration | Bundle | public | ID | ID | Cooperative | 2118 | 23537 | 1311 | 2667 | 47758 | 365 | 7685 | 147957 | 940 | 0 | 0 | 0 | 12470 | 219252 | 2616
Vigilante Electric Coop, IncID | 2018 | 23586 | Vigilante Electric Coop, Inc | NorthWestern Energy | Bundle | public | ID | ID | Cooperative | 18 | 125 | 35 | . | . | . | . | . | . | . | . | . | 18 | 125 | 35
Vigilante Electric Coop, IncMT | 2018 | 23586 | Vigilante Electric Coop, Inc | NorthWestern Energy | Bundle | public | WMT | MT | Cooperative | 9330 | 109177 | 8572 | 531 | 7713 | 150 | 3584 | 49483 | 1303 | . | . | . | 13445 | 166373 | 10025
Ravalli County Elec Coop, IncMT | 2018 | 26916 | Ravalli County Elec Coop, Inc | NorthWestern Energy | Bundle | public | WMT | MT | Cooperative | 13206.5 | 132071 | 9492 | 1111.6 | 12293 | 465 | 778.1 | 9642 | 595 | . | . | . | 15096.2 | 154006 | 10552
WAPA-- Western Area Power AdministrationMT | 2018 | 27000 | WAPA-- Western Area Power Administration | SWPP | Bundle |  |  | MT | Federal | 0 | 0 | 0 | 2330.9 | 96630 | 7 | 132.6 | 26171 | 8 | 0 | 0 | 0 | 2463.5 | 122801 | 15
Clatskanie Peoples Util DistOR | 2018 | 28541 | Clatskanie Peoples Util Dist | Bonneville Power Administration | Bundle | Public | OR | OR | Political Subdivision | 4993.3 | 72896 | 4001 | 913.1 | 17193 | 195 | 47867.3 | 929812 | 5 | 0 | 0 | 0 | 53773.7 | 1019901 | 4201
Talen Energy Marketing, LLCMT | 2018 | 28802 | Talen Energy Marketing, LLC | NorthWestern Energy | Energy |  | WMT | MT | Power Marketer | . | . | . | 9730 | 341861 | 5 | 31169 | 902796 | 7 | . | . | . | 40899 | 1244657 | 12
Emerald People's Utility DistOR | 2018 | 40437 | Emerald People's Utility Dist | PacifiCorp-West | Bundle | Public | OR | OR | Political Subdivision | 29356.4 | 285445 | 18936 | 10717.5 | 108536 | 1942 | 11115 | 230856 | 694 | . | . | . | 51188.9 | 624837 | 21572
Emerald People's Utility DistOR | 2018 | 40437 | Emerald People's Utility Dist | PacifiCorp-West | Delivery | Public | OR | OR | Political Subdivision | . | . | . | . | . | . | 307.3 | 165603 | 1 | . | . | . | 307.3 | 165603 | 1
Columbia River Peoples Ut DistOR | 2018 | 40438 | Columbia River Peoples Ut Dist | Bonneville Power Administration | Bundle | Public | OR | OR | Political Subdivision | 17540.3 | 215305 | 16994 | 8208.1 | 102200 | 2389 | 8273.7 | 164914 | 60 | 0 | 0 | 0 | 34022.1 | 482419 | 19443
PUD No 1 of Whatcom CountyWA | 2018 | 40456 | PUD No 1 of Whatcom County | Bonneville Power Administration | Bundle | Public | WA | WA | Political Subdivision | . | . | . | . | . | . | 11434 | 220310 | 1 | . | . | . | 11434 | 220310 | 1
Riverside Electric CooperativeID | 2018 | 56536 | Riverside Electric Cooperative | Idaho Power Company | Bundle | Public | ID | ID | Cooperative | 1002.9651 | 14844.7995 | 594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1398.1 | 21311 | 594
SolarCity CorporationOR | 2018 | 57313 | SolarCity Corporation | Bonneville Power Administration | Bundle |  | OR | OR | Behind the Meter | 6.5 | 107 | 18 | 101.2 | 1029 | 2 | 0 | 0 | 0 | 0 | 0 | . | 107.7 | 1136 | 20
SolarCity CorporationOR | 2018 | 57313 | SolarCity Corporation | PacifiCorp-West | Bundle |  | OR | OR | Behind the Meter | 249.9 | 3246 | 505 | 230.2 | 2953 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 480.1 | 6199 | 532
SolarCity CorporationOR | 2018 | 57313 | SolarCity Corporation | Portland General Electric Company | Bundle |  | OR | OR | Behind the Meter | 1577.5 | 20020 | 3167 | 305.5 | 3530 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 1883 | 23550 | 3186
SolarCity CorporationWA | 2018 | 57313 | SolarCity Corporation | Puget Sound Energy | Bundle |  | WA | WA | Behind the Meter | 77.7 | 599 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.7 | 599 | 102
PUD No 1 of Jefferson CountyWA | 2018 | 59013 | PUD No 1 of Jefferson County | Bonneville Power Administration | Bundle | Public | WA | WA | Political Subdivision | 23280 | 207266 | 17381 | 7443 | 69200 | 2475 | 5918 | 99970 | 21 | . | . | . | 36641 | 376436 | 19877
Longroad EnergyOR | 2018 | 61098 | Longroad Energy | Portland General Electric Company | Bundle |  | OR | OR | Behind the Meter | . | . | . | 155.3 | 1206 | 22 | . | . | . | . | . | . | 155.3 | 1206 | 22
Longroad EnergyOR | 2018 | 61098 | Longroad Energy | PacifiCorp-West | Bundle |  | OR | OR | Behind the Meter | . | . | . | 22.3 | 296 | 2 | . | . | . | . | . | . | 22.3 | 296 | 2
Surprise Valley Electrification Corp.CA | 2018 | 18260 | Surprise Valley Electrification Corp. | PacifiCorp-West | Bundle | Public | CA | CA | Cooperative | 3243.6 | 33890 | 2835 | 1026.4 | 10370 | 923 | 4581.2 | 53727 | 927 | 0 | 0 | 0 | 8851.2 | 97987 | 4685
Surprise Valley Electrification Corp.NV | 2018 | 18260 | Surprise Valley Electrification Corp. | PacifiCorp-West | Bundle | Public | NV | NV | Cooperative | 4.1 | 42 | 4 | 6.1 | 60 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 10.2 | 102 | 11
Harney Electric Coop, IncNV | 2018 | 11589 | Harney Electric Coop, Inc | Bonneville Power Administration | Bundle | public | NV | NV | Cooperative | 958 | 11367 | 599 | . | . | . | 6286.9 | 104685 | 735 | . | . | . | 7244.9 | 116052 | 1334
Lower Valley Energy IncWY | 2018 | 11273 | Lower Valley Energy Inc | Bonneville Power Administration | Bundle | Public | ID | WY | Cooperative | 28882.1 | 446564 | 20167 | 15738.7 | 246568 | 6046 | 1569.8 | 28918 | 175 | . | . | . | 46190.6 | 722050 | 26388
Wells Rural Electric CoNV | 2018 | 20332 | Wells Rural Electric Co | Bonneville Power Administration | Bundle | Public | NV | NV | Cooperative | 5527 | 54024 | 4327 | 4765 | 52345 | 945 | 31395 | 650434 | 151 | 0 | 0 | 0 | 41687 | 756803 | 5423
Wells Rural Electric CoNV | 2018 | 20332 | Wells Rural Electric Co | Bonneville Power Administration | Bundle | Public | UT | UT | Cooperative | 588 | 5408 | 504 | 1169 | 12822 | 205 | 1019 | 16929 | 4 | 0 | 0 | 0 | 2776 | 35159 | 713
Check Sums
Delivery | [11 empty] | 0.6018 | 30342.8825 | 1043090.6696 | 675.4663 | 45336.7303 | 4493339.6888 | 90.4342 | 0 | 0 | 0 | 75679.703 | 5536432.1638 | 766.5023
Energy | [11 empty] | 0 | 82362.1116 | 2462224.2973 | 143.6018 | 121345.1 | 4008365 | 38 | 0 | 0 | 0 | 203707.2116 | 6470589.2973 | 181.6018
Bundle | [11 empty] | 5814667.7447 | 4668800.1863 | 53462450.4156 | 789384.9401 | 2509171.1233 | 45777293.1077 | 87674.4154 | 3050.3 | 33133 | 8 | 13861703.703 | 165098173.037 | 6694008.8416
Note on A184: Charlie Grist: Added from BPA discussions. BPA serves all of the loads of these utilities, not just OR/WA/ID/MT
Note on A185: Charlie Grist: Added from BPA discussions. BPA serves all of the loads of these utilities, not just OR/WA/ID/MT
Note on A186: Charlie Grist: Added from BPA discussions. BPA serves all of the loads of these utilities, not just OR/WA/ID/MT
Note on A187: Charlie Grist: Added from BPA discussions. BPA serves all of the loads of these utilities, not just OR/WA/ID/MT
Note on A188: Charlie Grist: Added from BPA discussions. BPA serves all of the loads of these utilities, not just OR/WA/ID/MT
Note on A189: Charlie Grist: Wells Rural Electirc Co was added based on advise from BPA (Tony Kock). Wells is served by BPA and is part of BPA load. Data was extracted from EIA 2018
Yes, all of Lower Valley is served with BPA power and energy. Same with Surprise Valley and Wells. They are 100% BPA load following customers (they have a little local solar, etc., but they still have Load Following Requirements Contracts). There are others also in Nevada and Utah, e.g., Raft River and Harney Electric. We also serve some Montana utilities East of the Rockies, outside of W Montana, i.e., Glacier Electric and Vigilante. Note that we used to serve several coops far away in Eastern MT (some near North Dakota) under the old Hungry Horse Dam Act – they are on Charlie’s list. We stopped serving them in 2001 – the Hungry Horse Act requires that its power and energy stay in Montana, and for a long time, the W MT utilities were not large enough to consume that power. But, since 2001, the W MT utilities (plus Glacier and Vigilante) have become large enough to use all the Hungry Horse output. We ended our contracts with those six E MT coops at that time. They should be zeros on your spreadsheet because they are not in the region and also not served by BPA.
If I remember things correctly, more than half of our load and more than half of our firm Power regional customer are not in the BPA BA. The local BA doesn’t restrict our ability to be the Power supplier.
About forty percent of our load and half of our Power customers get served by other utility’s transmission lines, because they are located in other utility BA’s.
I’m completely OK sticking with the newer EIA data where there are differences. This has been a good reminder for me to update my data someday.
Frank
From: Koch,Tony A (BPA) - PEJD-SEATTLE <jakoch@bpa.gov> Sent: Friday, April 10, 2020 4:23 PM To: Charlie Grist <cgrist@nwcouncil.org> Cc: Brown,Frank E (BPA) - PES-SEATTLE <febrown@bpa.gov>; Aiona,Jessica L (BPA) - PEH-6 <jlaiona@bpa.gov> Subject: RE: Lower Valley + Surprise Valley + Wells + Harney
Thanks for sharing Charlie. Frank can confirm for sure, but I am 99+% sure BPA serves all loads for these utilities even if they cross state line and they do cross into other BA.
Our recommendation is that all the retail load from these customers should be included in the CVR potential, so recommend that you not filter our CA, NV, and WY loads shown in the EIA database. When you include all of the EIA data for those utilities you get a number that is close to Frank’s reference, so that makes sense. I agree to keep all the other discrepancies as is, using your 2018 EIA data.
I did a quick check on our records for applicable BA for each customer. Note that Harney is another utility that crosses into Nevada so the same should be done there and it will address the “purple” cell for Harney, that is, bring it into alignment with Frank’s number.
Lower Valley, BA = Rocky Mountain Power, its some form of PAC
Surprise Valley, BA = PACW
Wells Rural, BA = Idaho Power and Nevada Energy
Harney BA = BPA and Nevada Energy
From: Charlie Grist <cgrist@nwcouncil.org> Sent: Friday, April 10, 2020 3:36 PM To: Koch,Tony A (BPA) - PEJD-SEATTLE <jakoch@bpa.gov> Subject: [EXTERNAL] Lower Valley
Hi Tony: I was investigating the pink cells on your workbook that identify differences between Frank’s workbook and the EIA data.
Lower Valley: The difference is the Wyoming load of Lower Valley which we filtered out of the EIA. Should we put it back in?
Surprise Valley: Same thing but CA and NV load. But I notice Surprise Valley in the PACW balancing authority
EIA says Wells Rural is in NEVP balancing, but Frank said it is BPA load – confirming to add Wells
The remainder of differences appear to be the vintage of Frank’s estimate differing from the EIA vintage. Since many of Frank’s are older vintages, I will stick with EIA for the remiander

## Pivot 2018 EIA
[11 empty] | This pivot selected for "Delivery and Energy-Only" for the IOUs and for Power Marketer Sales in the "Region" as defined by western MT. Power Markter retail sales are almost exactly equal to IOU Delivery and Energy-Only sales to retail customers. Thus if we count Delivery and Energy-Only of the IOUs we do not need to count the Power Marketer Sales. |  |  |  |  | Seven Power marketers in the Region
[11 empty] | Bundle | (Multiple Items)
[11 empty] | region | (Multiple Items)
Row Labels | Count of Owner Type | Count of Owner Type | Column Labels |  |  |  | Column Labels |  |  |  |  | Column Labels |  |  |  | Owner Type | Power Marketer
Behind the Meter | 6 | Row Labels | Investor Owned | Power Marketer | Grand Total |  | Investor Owned |  | Power Marketer |  |  | Investor Owned |  | Power Marketer
Cooperative | 67 | ID | 3 |  | 3 | Row Labels | Count of Owner Type | Sum of Total Sales (MWh) | Count of Owner Type | Sum of Total Sales (MWh) | Row Labels | Count of Owner Type | Sum of Total Sales (MWh) | Count of Owner Type | Sum of Total Sales (MWh) | Row Labels | Count of Owner Type | Distinct Count of Owner Type2
Federal | 4 | MT | 4 | 2 | 6 | (blank) |  |  |  |  | Avangrid Renewables |  |  | 2 | 388321 | Avangrid Renewables | 2 | 1
Investor Owned | 16 | OR | 5 | 5 | 10 | Energy |  |  |  |  | BP Energy Company |  |  | 1 | 833304 | BP Energy Company | 1 | 1
Municipal | 41 | WA | 4 | 4 | 8 | Avangrid Renewables |  |  | 2 | 388321 | Calpine Energy Solutions, LLC |  |  | 3 | 1482883 | Calpine Energy Solutions, LLC | 3 | 1
Political Subdivision | 31 | Grand Total | 16 | 11 | 27 | ID |  |  |  |  | Constellation NewEnergy, Inc |  |  | 1 | 408825 | Constellation NewEnergy, Inc | 1 | 1
Power Marketer | 11 |  |  |  |  | Bundle |  |  |  |  | NorthWestern Corporation | 2 | 1225920.4611 |  |  | Shell Energy North America (US), L.P. | 2 | 1
Grand Total | 176 |  |  |  |  | Avista Corp | 1 | 2978419 |  |  | PacifiCorp | 1 | 393021 |  |  | Talen Energy Marketing, LLC | 1 | 1
[6 empty] | Idaho Power Co | 1 | 13907992 |  |  | Portland General Electric Company | 1 | 2035494 |  |  | Tenaska Power Services Co | 1 | 1
[6 empty] | PacifiCorp | 1 | 3643434 |  |  | Puget Sound Energy Inc | 1 | 2028727 |  |  | Grand Total | 11 | 1
[6 empty] | MT |  |  |  |  | Shell Energy North America (US), L.P. |  |  | 2 | 1321863
[6 empty] | Energy |  |  |  |  | Talen Energy Marketing, LLC |  |  | 1 | 1244657
[6 empty] | Tenaska Power Services Co |  |  | 1 | 478403 | Grand Total | 5 | 5683162.4611 | 10 | 5679853
OR
Bundle
[6 empty] | Idaho Power Co | 1 | 678530
[6 empty] | PacifiCorp | 1 | 12867233
[6 empty] | Portland General Electric Company | 1 | 17186002
Delivery
[6 empty] | PacifiCorp | 1 | 393021
[6 empty] | Portland General Electric Company | 1 | 2035494
Energy
[6 empty] | Calpine Energy Solutions, LLC |  |  | 2 | 1472660
[6 empty] | Constellation NewEnergy, Inc |  |  | 1 | 408825
[6 empty] | Shell Energy North America (US), L.P. |  |  | 1 | 166906
WA
Bundle
[6 empty] | Avista Corp | 1 | 5608063
[6 empty] | PacifiCorp | 1 | 3949116
[6 empty] | Puget Sound Energy Inc | 1 | 20697196
Delivery
[6 empty] | Puget Sound Energy Inc | 1 | 2028727
Energy
[6 empty] | BP Energy Company |  |  | 1 | 833304
[6 empty] | Calpine Energy Solutions, LLC |  |  | 1 | 10223
[6 empty] | Shell Energy North America (US), L.P. |  |  | 1 | 1154957
WMT
Bundle
[6 empty] | Avista Corp | 1 | 1058
[6 empty] | NorthWestern Corporation | 1 | 1811096.037
Delivery
[6 empty] | NorthWestern Corporation | 1 | 913587.1638
Energy
[6 empty] | NorthWestern Corporation | 1 | 312333.2973
[6 empty] | Talen Energy Marketing, LLC |  |  | 1 | 1244657
[6 empty] | Grand Total | 16 | 89011301.4981 | 11 | 6158256

## 2012 Sales Source Data
2012 Regional Sales Numbers
Source: Massoud Jourabchi, January 23, 2015. Modifications: None Purpose: Used to create the "20XX Sales" sheets, which are a Pivot Table of the respective "20XX Sales Source Data" sheets. The reason for the pivot table is to sum the sales for states with multiple rows due to either operating in different states (eg Avista in ID, WA, and WMT) or selling both bundled and delivered C&I energy (eg. PGE). Note: The column order between years 2012 and 2018 in these source files are not the same. It does not impact this work since it is the Pivot "20XX Sales" sheets that are used in the System Analysis sheet, but just FYI.
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Mapping | UTILITY_ID | YEAR | UTILITY_NAME | Service Type | Public/IOU | region | State | Owner Type | Res Revenue (000) | Res Sales (MWh) | Res Consumers (n) | Com Revenue (000) | Com Sales (MWh) | Com Consumers (n) | Ind Revenue (000) | Ind Sales (MWh) | Ind Consumers (n) | Trans Rev (000) | Trans Sales (MWh) | Trans Consumers (n) | Total Revenue (000) | Total Sales (MWh) | Total Consumers (n) | Public urban/non-urban
Alder Mutual Light Co, IncWA | 287 | 2012 | Alder Mutual Light Co, Inc | Bundle | Public | WA | WA | Cooperative | 246.6523 | 4192.5981 | 250.7832 | 25.3477 | 428.4019 | 27.2168 | 0 | 0 | 0 | 0 | 0 | 0 | 272 | 4621 | 278 | Rural
Avista CorpID | 20169 | 2012 | Avista Corp | Bundle | Private | ID | ID | Investor Owned | 102920 | 1164976 | 106519 | 87364 | 1008094 | 16900 | 63150 | 1185320 | 468 | 0 | 0 | 0 | 253434 | 3358390 | 123887
Avista CorpMT | 20169 | 2012 | Avista Corp | Bundle | Private | WMT | MT | Investor Owned | 13 | 162 | 9 | 31 | 337 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 499 | 23
Avista CorpWA | 20169 | 2012 | Avista Corp | Bundle | Private | WA | WA | Investor Owned | 212204 | 2443487 | 212164 | 207440 | 2156301 | 23552 | 56438 | 914328 | 927 | 0 | 0 | 0 | 476082 | 5514116 | 236643
Beartooth Electric Coop, IncMT | 1417 | 2012 | Beartooth Electric Coop, Inc | Bundle | Public | EMT | MT | Cooperative | 7681 | 44600 | 4943 | 1125 | 7810 | 400 | 234 | 2094 | 1 | . | . | . | 9040 | 54504 | 5344 | Rural
Benton Rural Electric AssnWA | 1625 | 2012 | Benton Rural Electric Assn | Bundle | Public | WA | WA | Cooperative | 17532 | 223469 | 11933 | 7490 | 118874 | 1360 | 12431 | 211980 | 1895 | . | . | . | 37453 | 554323 | 15188 | Rural
Big Bend Electric Coop, IncWA | 1723 | 2012 | Big Bend Electric Coop, Inc | Bundle | Public | WA | WA | Cooperative | 6468 | 97757 | 4600 | 20876 | 395899 | 4094 | . | 0 | . | . | . | . | 27344 | 493656 | 8694 | Rural
Big Flat Electric Coop IncMT | 1671 | 2012 | Big Flat Electric Coop Inc | Bundle | Public | EMT | MT | Cooperative | 2107.6248 | 18204.5308 | 1659.0074 | 418.226 | 3790.4868 | 201.8526 | 685.9492 | 5053.9824 | 33.14 | 0 | 0 | 0 | 3211.8 | 27049 | 1894 | Rural
Big Horn County Elec Coop, IncMT | 1683 | 2012 | Big Horn County Elec Coop, Inc | Bundle | Public | EMT | MT | Cooperative | 3824.2 | 38911 | 3102 | 2055 | 20022 | 543 | . | 0 | . | . | . | . | 5879.2 | 58933 | 3645 | Rural
Big Horn Rural Electric CoMT | 1675 | 2012 | Big Horn Rural Electric Co | Bundle | Public | EMT | MT | Cooperative | 45 | 354 | 36 | 306 | 2020 | 30 | 1759 | 13736 | 1 | . | . | 0 | 2110 | 16110 | 67 | Rural
Blachly-Lane Cnty Coop El AssnOR | 1736 | 2012 | Blachly-Lane Cnty Coop El Assn | Bundle | Public | OR | OR | Cooperative | 5272 | 51494 | 3242 | 2554 | 41345 | 375 | 3692 | 65684 | 4 | . | . | . | 11518 | 158523 | 3621 | Rural
Black Hills Power IncMT | 19545 | 2012 | Black Hills Power Inc | Bundle | Private | EMT | MT | Investor Owned | 5.2 | 61 | 12 | 114.3 | 1519 | 20 | 2464.7 | 48328 | 3 | . | . | . | 2584.2 | 49908 | 35
Bonneville Power AdminID | 1738 | 2012 | Bonneville Power Admin | Bundle | Public | ID | ID | Federal | . | . | . | . | 0 | . | 1 | 19796 | 1 | . | . | 0 | 1 | 19796 | 1
Bonneville Power AdminMT | 1738 | 2012 | Bonneville Power Admin | Delivery | Public | WMT | MT | Federal | . | . | . | . | 0 | . | 645 | 4067 | 1 | . | . | 0 | 645 | 4067 | 1
Bonneville Power AdminOR | 1738 | 2012 | Bonneville Power Admin | Bundle | Public | OR | OR | Federal | . | . | . | 167 | 4555 | 1 | . | 0 | 0 | . | . | 0 | 167 | 4555 | 1
Bonneville Power AdminWA | 1738 | 2012 | Bonneville Power Admin | Bundle | Public | WA | WA | Federal | . | . | . | 30023 | 858775 | 7 | 118325 | 6543152 | 2 | . | . | . | 148348 | 7401927 | 9
Bonneville Power AdminWA | 1738 | 2012 | Bonneville Power Admin | Delivery | Public | WA | WA | Federal | . | . | . | . | 0 | . | 1390 | 315200 | 1 | . | . | . | 1390 | 315200 | 1
BP Energy CompanyWA | 540 | 2012 | BP Energy Company | Energy | Unreg | WA | WA | Power Marketer | . | . | . | . | 0 | . | 21718 | 852781 | 3 | . | . | . | 21718 | 852781 | 3
Canby Utility BoardOR | 2955 | 2012 | Canby Utility Board | Bundle | Public | OR | OR | Municipal | 5027.6 | 78374 | 6049 | 3029.9 | 59383 | 685 | 1646.8 | 30927 | 12 | . | . | . | 9704.3 | 168684 | 6746 | Rural
Central Electric Coop IncOR | 3240 | 2012 | Central Electric Coop Inc | Bundle | Public | OR | OR | Cooperative | 35713 | 440371 | 27188 | 7062 | 97063 | 2579 | 6379 | 109654 | 1613 | . | . | . | 49154 | 647088 | 31380 | Rural
Central Lincoln People's Ut DtOR | 3264 | 2012 | Central Lincoln People's Ut Dt | Bundle | Public | OR | OR | Political Subdivision | 34004 | 433411 | 32744 | 13633 | 188055 | 5449 | 28118 | 689573 | 182 | . | . | . | 75755 | 1311039 | 38375 | Rural
City of AlbionID | 244 | 2012 | City of Albion | Bundle | Public | ID | ID | Municipal | 165.4346 | 1903.3496 | 180.5106 | 66.5654 | 845.6504 | 21.4894 | 0 | 0 | 0 | 0 | 0 | 0 | 232 | 2749 | 202 | Rural
City of AshlandOR | 907 | 2012 | City of Ashland | Bundle | Public | OR | OR | Municipal | 6483 | 90862 | 10172 | 5992 | 81286 | 1516 | . | 0 | . | . | . | . | 12475 | 172148 | 11688 | Rural
City of BandonOR | 1176 | 2012 | City of Bandon | Bundle | Public | OR | OR | Municipal | 2653 | 34629 | 2781 | 2179 | 27842 | 975 | 131 | 1333 | 3 | . | . | . | 4963 | 63804 | 3759 | Rural
City of BlaineWA | 1818 | 2012 | City of Blaine | Bundle | Public | WA | WA | Municipal | 1621 | 24042 | 2490 | 2915 | 39249 | 517 | 706 | 9519 | 13 | . | . | . | 5242 | 72810 | 3020 | Rural
City of Bonners FerryID | 1956 | 2012 | City of Bonners Ferry | Bundle | Public | ID | ID | Municipal | 1793.408 | 24225.0273 | 1914 | 1536.7206 | 23244.7546 | 659 | 956.8714 | 18576.2182 | 20 | 0 | 0 | 0 | 4287 | 66046 | 2593 | Rural
City of BurleyID | 2545 | 2012 | City of Burley | Bundle | Public | ID | ID | Municipal | 3143 | 46454 | 3791 | 3706 | 64345 | 723 | 0 | 0 | 0 | 0 | 0 | 0 | 6849 | 110799 | 4514 | Rural
City of Cascade LocksOR | 3136 | 2012 | City of Cascade Locks | Bundle | Public | OR | OR | Municipal | 709.9052 | 8082.5202 | 734.779 | 779.0948 | 9656.4798 | 73.221 | 0 | 0 | 0 | 0 | 0 | 0 | 1489 | 17739 | 808 | Rural
City of CentraliaWA | 3295 | 2012 | City of Centralia | Bundle | Public | WA | WA | Municipal | 8923.7 | 117052 | 8415 | 3069.2 | 36015 | 1426 | 8217.9 | 107760 | 141 | . | . | . | 20210.8 | 260827 | 9982 | Rural
City of CheneyWA | 3420 | 2012 | City of Cheney | Bundle | Public | WA | WA | Municipal | 3224.5 | 52056 | 4507 | 3429.7 | 70429 | 410 | 468.3 | 9741 | 8 | . | . | . | 7122.5 | 132226 | 4925 | Rural
City of ChewelahWA | 3459 | 2012 | City of Chewelah | Bundle | Public | WA | WA | Municipal | 1014.4387 | 12568.3572 | 1085.2696 | 902.5613 | 10231.6428 | 204.7304 | 0 | 0 | 0 | 0 | 0 | 0 | 1917 | 22800 | 1290 | Rural
City of Coulee DamWA | 4414 | 2012 | City of Coulee Dam | Bundle | Public | WA | WA | Municipal | 528.2784 | 9446.4928 | 515.1371 | 401.7216 | 7187.5072 | 81.8629 | 0 | 0 | 0 | 0 | 0 | 0 | 930 | 16634 | 597 | Rural
City of DecloID | 7084 | 2012 | City of Declo | Bundle | Public | ID | ID | Municipal | 107.6988 | 1641.4379 | 109 | 60.7238 | 994.3001 | 14 | 19.4774 | 366.262 | 11 | 0 | 0 | 0 | 187.9 | 3002 | 134 | Rural
City of DrainOR | 5354 | 2012 | City of Drain | Bundle | Public | OR | OR | Municipal | 626.1406 | 7479.5778 | 513.8911 | 323.3107 | 3461.0353 | 156.2308 | 352.2487 | 4817.3869 | 6.8781 | 0 | 0 | 0 | 1301.7 | 15758 | 677 | Rural
City of EllensburgWA | 6149 | 2012 | City of Ellensburg | Bundle | Public | WA | WA | Municipal | 5726 | 75016 | 7989 | 6639 | 116613 | 1541 | 655 | 10519 | 1 | 0 | 0 | 0 | 13020 | 202148 | 9531 | Rural
City of Forest GroveOR | 6582 | 2012 | City of Forest Grove | Bundle | Public | OR | OR | Municipal | 7134.2 | 109097 | 8159 | 1415 | 20915 | 810 | 5333.6 | 102541 | 141 | . | . | . | 13882.8 | 232553 | 9110 | Rural
City of HermistonOR | 8515 | 2012 | City of Hermiston | Bundle | Public | OR | OR | Municipal | 3577 | 51129 | 4472 | 3480 | 53502 | 816 | 0 | 0 | 0 | 0 | 0 | 0 | 7057 | 104631 | 5288 | Rural
City of McClearyWA | 11965 | 2012 | City of McCleary | Bundle | Public | WA | WA | Municipal | 1126.6257 | 15655.4091 | 920.8984 | 422.5628 | 4308.0532 | 101.0986 | 641.6115 | 9721.5377 | 3.0029 | 0 | 0 | 0 | 2190.8 | 29685 | 1025 | Rural
City of Milton-FreewaterOR | 12615 | 2012 | City of Milton-Freewater | Bundle | Public | OR | OR | Municipal | 3646 | 60331 | 3504 | 828 | 14487 | 500 | 1738 | 30391 | 340 | . | . | . | 6212 | 105209 | 4344 | Rural
City of MiltonWA | 12616 | 2012 | City of Milton | Bundle | Public | WA | WA | Municipal | 2723.8797 | 41313.9366 | 3193.5769 | 1278.1203 | 17681.0634 | 205.4231 | 0 | 0 | 0 | 0 | 0 | 0 | 4002 | 58995 | 3399 | Rural
City of MinidokaID | 12609 | 2012 | City of Minidoka | Bundle | Public | ID | ID | Municipal | 45.5 | 827.8355 | 45.9574 | 6.5 | 40.1645 | 2.0426 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 868 | 48 | Rural
City of MonmouthOR | 12789 | 2012 | City of Monmouth | Bundle | Public | OR | OR | Municipal | 3760.7 | 43642 | 3994 | 331.2 | 3758 | 213 | 1675 | 21919 | 61 | . | . | . | 5766.9 | 69319 | 4268 | Rural
City of PlummerID | 15297 | 2012 | City of Plummer | Bundle | Public | ID | ID | Municipal | 828.6813 | 9994.5608 | 826.2331 | 568.4595 | 8646.9 | 163.59 | 699.6592 | 13794.5392 | 5.1769 | 0 | 0 | 0 | 2096.8 | 32436 | 995 | Rural
City of RichlandWA | 15979 | 2012 | City of Richland | Bundle | Public | WA | WA | Municipal | 22913 | 330864 | 22846 | 16527 | 346643 | 2870 | 6912 | 170011 | 11 | . | . | . | 46352 | 847518 | 25727 | Urban
City of Soda SpringsID | 17493 | 2012 | City of Soda Springs | Bundle | Public | ID | ID | Municipal | 1060.3415 | 13569.9547 | 1449.8155 | 896.5976 | 13229.6254 | 325.0979 | 24.961 | 368.4199 | 9.0866 | 0 | 0 | 0 | 1981.9 | 27168 | 1784 | Rural
City of SpringfieldOR | 17839 | 2012 | City of Springfield | Bundle | Public | OR | OR | Municipal | 21526 | 386504 | 27848 | 14565 | 262900 | 3834 | 7855 | 162504 | 13 | . | . | . | 43946 | 811908 | 31695 | Urban
City of SumasWA | 18282 | 2012 | City of Sumas | Bundle | Public | WA | WA | Municipal | 352.8579 | 5513.869 | 545.6277 | 297.1958 | 4826.1305 | 126.4502 | 1161.9462 | 19159.0005 | 17.9221 | 0 | 0 | 0 | 1812 | 29499 | 690 | Rural
City of TroyMT | 19236 | 2012 | City of Troy | Bundle | Public | WMT | MT | Municipal | 763.62 | 12816.6459 | 846.9421 | 297.972 | 5649.7169 | 124.0165 | 6.408 | 71.6372 | 5.0413 | 0 | 0 | 0 | 1068 | 18538 | 976 | Rural
City of WeiserID | 20297 | 2012 | City of Weiser | Bundle | Public | ID | ID | Municipal | 1663.0828 | 25177.6889 | 2405.8453 | 773.3463 | 14221.4739 | 326.1481 | 476.5709 | 9836.8372 | 1.0066 | 0 | 0 | 0 | 2913 | 49236 | 2733 | Rural
Clatskanie Peoples Util DistOR | 28541 | 2012 | Clatskanie Peoples Util Dist | Bundle | Public | OR | OR | Political Subdivision | 3499 | 72364 | 4036 | 1347 | 26226 | 569 | 37167 | 872001 | 4 | 0 | 0 | 0 | 42013 | 970591 | 4609 | Rural
Clear Lake Cogeneration LPID | 3775 | 2012 | Clear Lake Cogeneration LP | Bundle | Unreg | ID | ID | Power Marketer | . | . | . | . | 0 | . | 4916 | 218452 | 1 | . | . | . | 4916 | 218452 | 1
Clearwater Power CompanyID | 3739 | 2012 | Clearwater Power Company | Bundle | Public | ID | ID | Cooperative | 12029.9 | 117033 | 8519 | 2109.1 | 25204 | 738 | 1226 | 23408 | 5 | . | . | . | 15365 | 165645 | 9262 | Rural
Clearwater Power CompanyOR | 3739 | 2012 | Clearwater Power Company | Bundle | Public | OR | OR | Cooperative | 149.9 | 1419 | 135 | 25.8 | 250 | 21 | . | 0 | 0 | . | . | 0 | 175.7 | 1669 | 156 | Rural
Clearwater Power CompanyWA | 3739 | 2012 | Clearwater Power Company | Bundle | Public | WA | WA | Cooperative | 1031.4 | 9865 | 808 | 252.5 | 2790 | 132 | 47.2 | 1069 | 1 | . | . | 0 | 1331.1 | 13724 | 941 | Rural
Columbia Basin Elec Cooperative, IncOR | 4005 | 2012 | Columbia Basin Elec Cooperative, Inc | Bundle | Public | OR | OR | Cooperative | 3744.6 | 41387 | 3092 | 1932 | 27649 | 513 | 1857.4 | 35848 | 233 | 0 | 0 | 0 | 7534 | 104884 | 3838 | Rural
Columbia Power Coop Assn IncOR | 4008 | 2012 | Columbia Power Coop Assn Inc | Bundle | Public | OR | OR | Cooperative | 1279.4 | 13912 | 1329 | 405 | 5034 | 236 | 353 | 5138 | 249 | . | . | 0 | 2037.4 | 24084 | 1814 | Rural
Columbia River Peoples Ut DistOR | 40438 | 2012 | Columbia River Peoples Ut Dist | Bundle | Public | OR | OR | Political Subdivision | 14259 | 211529 | 16111 | 6346.5 | 88068 | 2461 | 6861.2 | 161465 | 65 | . | . | . | 27466.7 | 461062 | 18637 | Rural
Columbia Rural Elec Assn, IncOR | 4041 | 2012 | Columbia Rural Elec Assn, Inc | Bundle | Public | OR | OR | Cooperative | 71.7 | 757 | 44 | 28.4 | 167 | 29 | 324.3 | 4923 | 68 | . | . | 0 | 424.4 | 5847 | 141 | Rural
Columbia Rural Elec Assn, IncWA | 4041 | 2012 | Columbia Rural Elec Assn, Inc | Bundle | Public | WA | WA | Cooperative | 4500.7 | 47381 | 2985 | 3868.7 | 46742 | 1243 | 11677.9 | 198368 | 531 | . | . | . | 20047.3 | 292491 | 4759 | Rural
ConocoPhillips CompanyMT | 5470 | 2012 | ConocoPhillips Company | Energy | Unreg | EMT | MT | Power Marketer | 0 | 0 | 0 | 0 | 0 | 0 | 11907 | 384715 | 3 | 0 | 0 | 0 | 11907 | 384715 | 3
Constellation NewEnergy, IncOR | 13374 | 2012 | Constellation NewEnergy, Inc | Energy | Unreg | OR | OR | Power Marketer | 0 | 0 | 0 | 5204.7 | 63284 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 5204.7 | 63284 | 1
Consumers Power, IncOR | 4743 | 2012 | Consumers Power, Inc | Bundle | Public | OR | OR | Cooperative | 23942.7 | 269083 | 19723 | 7338.4 | 104203 | 1726 | 1473.5 | 19419 | 565 | . | . | . | 32754.6 | 392705 | 22014 | Rural
Coos-Curry Electric Coop, IncOR | 4317 | 2012 | Coos-Curry Electric Coop, Inc | Bundle | Public | OR | OR | Cooperative | 18867.5 | 196349 | 14938 | 8295.7 | 94495 | 2051 | 3580.4 | 47835 | 463 | . | . | . | 30743.6 | 338679 | 17452 | Rural
Douglas Electric Coop, IncOR | 5327 | 2012 | Douglas Electric Coop, Inc | Bundle | Public | OR | OR | Cooperative | 11268 | 120998 | 9027 | 1758 | 18649 | 744 | 525 | 6765 | 7 | . | . | . | 13551 | 146412 | 9778 | Rural
East End Mutual Elec Co LtdID | 5584 | 2012 | East End Mutual Elec Co Ltd | Bundle | Public | ID | ID | Cooperative | 970.7317 | 15333.3333 | 487.7735 | 478.2683 | 7666.6667 | 239.2265 | 0 | 0 | 0 | 0 | 0 | 0 | 1449 | 23000 | 727 | Rural
Elmhurst Mutual Power & Light CoWA | 5832 | 2012 | Elmhurst Mutual Power & Light Co | Bundle | Public | WA | WA | Cooperative | 12390 | 220710 | 13288 | 2008 | 39861 | 647 | . | 0 | . | . | . | . | 14398 | 260571 | 13935 | Rural
Emerald People's Utility DistOR | 40437 | 2012 | Emerald People's Utility Dist | Bundle | Public | OR | OR | Political Subdivision | 23770.3 | 280175 | 18118 | 7431.9 | 86512 | 1814 | 3170.6 | 46886 | 553 | 0 | 0 | 0 | 34372.8 | 413573 | 20485 | Rural
Emerald People's Utility DistOR | 40437 | 2012 | Emerald People's Utility Dist | Delivery | Public | OR | OR | Political Subdivision | 0 | 0 | 0 | 0 | 0 | 0 | 607.3 | 158031 | 1 | 0 | 0 | 0 | 607.3 | 158031 | 1 | Rural
Eugene City ofOR | 6022 | 2012 | Eugene City of | Bundle | Public | OR | OR | Municipal | 90785 | 941922 | 79626 | 67004 | 872419 | 9712 | 25721 | 550270 | 4 | 0 | 0 | 0 | 183510 | 2364611 | 89342 | Urban
Fall River Rural Elec Coop IncID | 6169 | 2012 | Fall River Rural Elec Coop Inc | Bundle | Public | ID | ID | Cooperative | 14097 | 130972 | 11011 | 6931 | 100011 | 2210 | . | 0 | . | . | . | . | 21028 | 230983 | 13221 | Rural
Fall River Rural Elec Coop IncMT | 6169 | 2012 | Fall River Rural Elec Coop Inc | Bundle | Public | WMT | MT | Cooperative | 1735 | 15995 | 1371 | 2232 | 29952 | 484 | . | 0 | . | . | . | . | 3967 | 45947 | 1855 | Rural
Farmers Electric Company, LtdID | 6155 | 2012 | Farmers Electric Company, Ltd | Bundle | Public | ID | ID | Cooperative | 93.4131 | 1875.4395 | 99.1736 | 93.4131 | 1975.1969 | 11.9008 | 10.1737 | 183.3636 | 8.9256 | 0 | 0 | 0 | 197 | 4034 | 120 | Rural
Fergus Electric Coop, IncMT | 21513 | 2012 | Fergus Electric Coop, Inc | Bundle | Public | EMT | MT | Cooperative | 8900 | 57000 | 5816 | 13100 | 138000 | 236 | 400 | 3000 | 94 | . | . | . | 22400 | 198000 | 6146 | Rural
Flathead Electric Coop IncMT | 6395 | 2012 | Flathead Electric Coop Inc | Bundle | Public | WMT | MT | Cooperative | 53850 | 674819 | 51979 | 27431 | 427906 | 9561 | 12006 | 244791 | 81 | . | . | . | 93287 | 1347516 | 61621 | Urban
Glacier Electric Coop, IncMT | 7262 | 2012 | Glacier Electric Coop, Inc | Bundle | Public | WMT | MT | Cooperative | 6732 | 68147 | 5790 | 6130 | 81600 | 1676 | 1238 | 19394 | 5 | . | . | . | 14100 | 169141 | 7471 | Rural
Goldenwest Electric Coop, IncMT | 7318 | 2012 | Goldenwest Electric Coop, Inc | Bundle | Public | EMT | MT | Cooperative | 718.7264 | 5855.3944 | 711.8088 | 102.5736 | 773.6056 | 9.1912 | 0 | 0 | 0 | 0 | 0 | 0 | 821.3 | 6629 | 721 | Rural
Grand Electric Coop, IncMT | 7484 | 2012 | Grand Electric Coop, Inc | Bundle | Public | EMT | MT | Cooperative | 11 | 117 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 117 | 15 | Rural
Harney Electric Coop, IncOR | 11589 | 2012 | Harney Electric Coop, Inc | Bundle | Public | OR | OR | Cooperative | 1256 | 17596 | 945 | . | 0 | . | 3638.2 | 64794 | 1468 | . | . | . | 4894.2 | 82390 | 2413 | Rural
Heyburn City ofID | 8532 | 2012 | Heyburn City of | Bundle | Public | ID | ID | Municipal | 1083.3494 | 19715.932 | 1376.3624 | 465.6662 | 6790.3992 | 119.5504 | 762.8844 | 13364.6688 | 4.0872 | 0 | 0 | 0 | 2311.9 | 39871 | 1500 | Rural
Hill County Electric Coop, IncMT | 8632 | 2012 | Hill County Electric Coop, Inc | Bundle | Public | EMT | MT | Cooperative | 4893.1 | 39008 | 3566 | 2618.1 | 26909 | 190 | 4551.5 | 59591 | 3 | . | . | . | 12062.7 | 125508 | 3759 | Rural
Hinson Power Company LLCMT | 8936 | 2012 | Hinson Power Company LLC | Bundle | Unreg | WMT | MT | Power Marketer | 0 | 0 | 0 | 0 | 0 | 0 | 180.5 | 8783 | 1 | 0 | 0 | 0 | 180.5 | 8783 | 1
Hood River Electric CoopOR | 8830 | 2012 | Hood River Electric Coop | Bundle | Public | OR | OR | Cooperative | 3768.9 | 53201 | 3262 | 394 | 5606 | 215 | 2761.3 | 49640 | 208 | . | . | . | 6924.2 | 108447 | 3685 | Rural
Idaho Cnty L&P Coop Assn, IncID | 9186 | 2012 | Idaho Cnty L&P Coop Assn, Inc | Bundle | Public | ID | ID | Cooperative | 4292.6243 | 40455.6486 | 3493.2615 | 791.0668 | 8115.6695 | 247.6415 | 28.2089 | 197.6819 | 9.097 | 0 | 0 | 0 | 5111.9 | 48769 | 3750 | Rural
Idaho Falls City ofID | 9187 | 2012 | Idaho Falls City of | Bundle | Public | ID | ID | Municipal | 19212 | 279649 | 22449 | 16420 | 261215 | 3705 | 4158 | 87016 | 7 | 0 | 0 | 0 | 39790 | 627880 | 26161 | Urban
Idaho Power CoID | 9191 | 2012 | Idaho Power Co | Bundle | Private | ID | ID | Investor Owned | 415210.9 | 4854236 | 400291 | 230715.8 | 3716773 | 62249 | 265534 | 4893132 | 17344 | 0 | 0 | 0 | 911460.7 | 13464141 | 479884
Idaho Power CoOR | 9191 | 2012 | Idaho Power Co | Bundle | Private | OR | OR | Investor Owned | 16344.6 | 185122 | 13319 | 10803.1 | 148194 | 3349 | 16944 | 287859 | 1730 | 0 | 0 | 0 | 44091.7 | 621175 | 18398
Inland Power & Light CompanyID | 8699 | 2012 | Inland Power & Light Company | Bundle | Public | ID | ID | Cooperative | 1736 | 23474 | 1561 | 221 | 2973 | 99 | 1 | 4 | 4 | . | . | . | 1958 | 26451 | 1664 | Rural
Inland Power & Light CompanyWA | 8699 | 2012 | Inland Power & Light Company | Bundle | Public | WA | WA | Cooperative | 43042 | 591806 | 34465 | 8071 | 117436 | 2149 | 6655 | 117121 | 525 | . | . | . | 57768 | 826363 | 37139 | Rural
JP MorganOR | 56528 | 2012 | JP Morgan | Energy | Unreg | OR | OR | Power Marketer | 0 | 0 | 0 | 0 | 0 | 0 | 3088 | 158044 | 1 | 0 | 0 | 0 | 3088 | 158044 | 1
JP MorganWA | 56528 | 2012 | JP Morgan | Energy | Unreg | WA | WA | Power Marketer | 0 | 0 | 0 | 0 | 0 | 0 | 41997 | 602987 | 2 | 0 | 0 | 0 | 41997 | 602987 | 2
Kootenai Electric Coop IncID | 10454 | 2012 | Kootenai Electric Coop Inc | Bundle | Public | ID | ID | Cooperative | 23534.4 | 279946 | 20571 | 8281.6 | 102202 | 1672 | 1322.9 | 28502 | 46 | 0 | 0 | 0 | 33138.9 | 410650 | 22289 | Rural
Kootenai Electric Coop IncWA | 10454 | 2012 | Kootenai Electric Coop Inc | Bundle | Public | WA | WA | Cooperative | 155.4 | 1964 | 77 | 0.1 | 1 | 1 | 0.4 | 3 | 1 | 0 | 0 | 0 | 155.9 | 1968 | 79 | Rural
Lakeview Light & PowerWA | 10627 | 2012 | Lakeview Light & Power | Bundle | Public | WA | WA | Cooperative | 8312 | 114535 | 9380 | 10865 | 149774 | 2054 | . | 0 | . | . | . | . | 19177 | 264309 | 11434 | Rural
Lane Electric Coop IncOR | 10681 | 2012 | Lane Electric Coop Inc | Bundle | Public | OR | OR | Cooperative | 17789.9 | 191562 | 11884 | 2949.8 | 32356 | 844 | 270.3 | 3776 | 1 | . | . | . | 21010 | 227694 | 12729 | Rural
Lincoln Electric Coop, IncMT | 11022 | 2012 | Lincoln Electric Coop, Inc | Bundle | Public | WMT | MT | Cooperative | 6063 | 71230 | 4684 | 1906 | 26060 | 695 | 860 | 11010 | 4 | . | . | . | 8829 | 108300 | 5383 | Rural
Lost River Electric Coop IncID | 11211 | 2012 | Lost River Electric Coop Inc | Bundle | Public | ID | ID | Cooperative | 2482.6089 | 31934.353 | 1800.4254 | 335.7453 | 4667.0573 | 215.7285 | 2608.6458 | 41280.5897 | 604.8462 | 0 | 0 | 0 | 5427 | 77882 | 2621 | Rural
Lower Valley Energy IncID | 11273 | 2012 | Lower Valley Energy Inc | Bundle | Public | ID | ID | Cooperative | 784 | 13073 | 1265 | 158 | 2690 | 317 | 1803 | 46527 | 39 | . | . | . | 2745 | 62290 | 1621 | Rural
Lower Yellowstone R E A, IncMT | 11272 | 2012 | Lower Yellowstone R E A, Inc | Bundle | Public | EMT | MT | Cooperative | 2835 | 37263 | 2813 | 2683 | 29379 | 774 | 8648 | 86946 | 979 | . | . | . | 14166 | 153588 | 4566 | Rural
Marias River Electric Coop IncMT | 11643 | 2012 | Marias River Electric Coop Inc | Bundle | Public | EMT | MT | Cooperative | 2354.4 | 29843 | 2512 | 4431 | 56393 | 1326 | . | 0 | . | . | . | . | 6785.4 | 86236 | 3838 | Rural
McCone Electric Coop IncMT | 11989 | 2012 | McCone Electric Coop Inc | Bundle | Public | EMT | MT | Cooperative | 5377.4 | 43344 | 4539 | 2221.2 | 21603 | 514 | 214.1 | 1744 | 70 | . | . | . | 7812.7 | 66691 | 5123 | Rural
McKenzie Electric Coop IncMT | 12087 | 2012 | McKenzie Electric Coop Inc | Bundle | Public | EMT | MT | Cooperative | 83.2 | 749 | 124 | 0.3 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 83.5 | 750 | 125 | Rural
McMinnville City ofOR | 12187 | 2012 | McMinnville City of | Bundle | Public | OR | OR | Municipal | 10950 | 204187 | 13068 | 11851 | 177463 | 3150 | 12947 | 335477 | 52 | 0 | 0 | 0 | 35748 | 717127 | 16270 | Urban
Midstate Electric Coop, IncOR | 12439 | 2012 | Midstate Electric Coop, Inc | Bundle | Public | OR | OR | Cooperative | 17881 | 231394 | 16160 | 7428 | 112104 | 2052 | 1813 | 28081 | 3 | . | . | . | 27122 | 371579 | 18215 | Rural
Mid-Yellowstone Elec Coop, IncMT | 12463 | 2012 | Mid-Yellowstone Elec Coop, Inc | Bundle | Public | EMT | MT | Cooperative | 2108.3 | 13438 | 1020 | 497.4 | 3713 | 204 | 1588 | 11883 | 732 | . | . | . | 4193.7 | 29034 | 1956 | Rural
Missoula Electric Coop, IncID | 12692 | 2012 | Missoula Electric Coop, Inc | Bundle | Public | ID | ID | Cooperative | 49.2 | 469 | 36 | 69.8 | 781 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 119 | 1250 | 56 | Rural
Missoula Electric Coop, IncMT | 12692 | 2012 | Missoula Electric Coop, Inc | Bundle | Public | WMT | MT | Cooperative | 13974.1 | 149863 | 12460 | 3384.8 | 40154 | 1284 | 1306.2 | 18593 | 272 | 0 | 0 | 0 | 18665.1 | 208610 | 14016 | Rural
Modern Electric Water CompanyWA | 12744 | 2012 | Modern Electric Water Company | Bundle | Public | WA | WA | Cooperative | 5538 | 96953 | 8218 | 6297 | 112103 | 1637 | . | 0 | . | . | . | . | 11835 | 209056 | 9855 | Rural
Montana-Dakota Utilities CoMT | 12199 | 2012 | Montana-Dakota Utilities Co | Bundle | Private | EMT | MT | Investor Owned | 16042 | 190509 | 19390 | 17694 | 251430 | 5478 | 17062 | 320527 | 143 | 0 | 0 | 0 | 50798 | 762466 | 25011
Nespelem Valley Elec Coop, IncWA | 13387 | 2012 | Nespelem Valley Elec Coop, Inc | Bundle | Public | WA | WA | Cooperative | 1578.6454 | 21214.3563 | 1207.3594 | 999.7711 | 14765.9723 | 257.6374 | 813.5835 | 13528.6714 | 98.0032 | 0 | 0 | 0 | 3392 | 49509 | 1563 | Rural
Noble Americas Energy Solutions LLCOR | 16840 | 2012 | Noble Americas Energy Solutions LLC | Energy | Unreg | OR | OR | Power Marketer | 0 | 0 | 0 | 31984 | 904381 | 40 | 15341.8 | 434140 | 7 | 0 | 0 | 0 | 47325.8 | 1338521 | 47
Northern Lights, IncID | 13758 | 2012 | Northern Lights, Inc | Bundle | Public | ID | ID | Cooperative | 15212.6 | 165504 | 13810 | 2972.7 | 34504 | 742 | 829 | 18342 | 4 | . | . | . | 19014.3 | 218350 | 14556 | Rural
Northern Lights, IncMT | 13758 | 2012 | Northern Lights, Inc | Bundle | Public | WMT | MT | Cooperative | 3920.3 | 41489 | 3717 | 573.6 | 6639 | 250 | 1909.8 | 48286 | 5 | . | . | . | 6403.7 | 96414 | 3972 | Rural
Northern Lights, IncWA | 13758 | 2012 | Northern Lights, Inc | Bundle | Public | WA | WA | Cooperative | 11.8 | 112 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.8 | 112 | 15 | Rural
Northern Wasco County PUDOR | 13788 | 2012 | Northern Wasco County PUD | Bundle | Public | OR | OR | Political Subdivision | 8146.7 | 139695 | 9198 | 990.9 | 17549 | 431 | 16507.6 | 393231 | 226 | . | . | . | 25645.2 | 550475 | 9855 | Rural
NorthWestern CorporationMT | 12825 | 2012 | NorthWestern Corporation | Bundle | Private | EMT | MT | Investor Owned | 188720.0872 | 1755485.409 | 204178.1973 | 228758.7742 | 2363426.7843 | 47906.2327 | 28773.8449 | 1781094.2779 | 948.7266 | 0 | 0 | 0 | 446252.7063 | 5900006.4712 | 234390.5475
NorthWestern CorporationMT | 12825 | 2012 | NorthWestern Corporation | Bundle | Private | WMT | MT | Investor Owned | 64363.6128 | 599222.591 | 69628.8027 | 89060.2258 | 884308.2157 | 17924.7673 | 19479.4551 | 1205773.7221 | 642.2734 | 0 | 0 | 0 | 172903.2937 | 2689304.5288 | 106838.4525
NorVal Electric Cooperative, IncMT | 13749 | 2012 | NorVal Electric Cooperative, Inc | Bundle | Public | EMT | MT | Cooperative | 3768.7847 | 29622.1978 | 1923.363 | 2897.6 | 17547.1567 | 1327.5772 | 577.6153 | 5380.6456 | 4.0599 | 0 | 0 | 0 | 7244 | 52550 | 3255 | Rural
Ohop Mutual Light Company, IncWA | 14012 | 2012 | Ohop Mutual Light Company, Inc | Bundle | Public | WA | WA | Cooperative | 5893 | 74133 | 4065 | 290 | 3897 | 112 | 5 | 52 | 11 | . | . | . | 6188 | 78082 | 4188 | Rural
Okanogan County Elec Coop, IncWA | 14074 | 2012 | Okanogan County Elec Coop, Inc | Bundle | Public | WA | WA | Cooperative | 3852.5 | 37438 | 3212 | 1038.1 | 16803 | 300 | . | 0 | . | . | . | . | 4890.6 | 54241 | 3512 | Rural
Orcas Power & Light CoopWA | 14170 | 2012 | Orcas Power & Light Coop | Bundle | Public | WA | WA | Cooperative | 14475 | 140026 | 12757 | 5133 | 55140 | 1928 | . | 0 | . | . | . | . | 19608 | 195166 | 14685 | Rural
Oregon Trail El Cons Coop, IncOR | 14109 | 2012 | Oregon Trail El Cons Coop, Inc | Bundle | Public | OR | OR | Cooperative | 24621 | 280932 | 25033 | 16461 | 244065 | 5267 | 5508 | 106611 | 9 | . | . | . | 46590 | 631608 | 30309 | Rural
Pacific Public Utility District No 2WA | 14324 | 2012 | Pacific Public Utility District No 2 | Bundle | Public | WA | WA | Political Subdivision | 13876.7 | 179572 | 14998 | 6845.7 | 83201 | 2261 | 1158.8 | 23082 | 2 | . | . | . | 21881.2 | 285855 | 17261 | Rural
PacifiCorpID | 14354 | 2012 | PacifiCorp | Bundle | Private | ID | ID | Investor Owned | 70090.7 | 675655 | 57890 | 38404.3 | 439776 | 8673 | 153750.8 | 2402196 | 5550 | 0 | 0 | 0 | 262245.8 | 3517627 | 72113
PacifiCorpOR | 14354 | 2012 | PacifiCorp | Bundle | Private | OR | OR | Investor Owned | 561148.3 | 5405577 | 473821 | 427944.8 | 4998437 | 76659 | 161193.3 | 2358130 | 9552 | 1329.5 | 16638 | 1 | 1151615.9 | 12778782 | 560033
PacifiCorpOR | 14354 | 2012 | PacifiCorp | Delivery | Private | OR | OR | Investor Owned | 0 | 0 | 0 | 5152.8 | 136162 | 64 | 1474.6 | 50641 | 2 | 0 | 0 | 0 | 6627.4 | 186803 | 66
PacifiCorpWA | 14354 | 2012 | PacifiCorp | Bundle | Private | WA | WA | Investor Owned | 131372.3 | 1596276 | 104224 | 111956.9 | 1457584 | 17921 | 63476 | 988038 | 5749 | 0 | 0 | 0 | 306805.2 | 4041898 | 127894
Park Electric Coop IncMT | 14500 | 2012 | Park Electric Coop Inc | Bundle | Public | EMT | MT | Cooperative | 6333.9 | 65094 | 5181 | 552.6 | 7610 | 85 | 6248.2 | 81627 | 292 | . | . | . | 13134.7 | 154331 | 5558 | Rural
Parkland Light & Water CompanyWA | 14505 | 2012 | Parkland Light & Water Company | Bundle | Public | WA | WA | Cooperative | 3360 | 55916 | 3862 | 3297 | 60861 | 591 | . | 0 | . | . | . | . | 6657 | 116777 | 4453 | Rural
Peninsula Light CompanyWA | 14668 | 2012 | Peninsula Light Company | Bundle | Public | WA | WA | Cooperative | 36721 | 423183 | 27232 | 12418 | 156492 | 3633 | 0 | 0 | . | 0 | 0 | . | 49139 | 579675 | 30865 | Urban
Port Angeles City ofWA | 15231 | 2012 | Port Angeles City of | Bundle | Public | WA | WA | Municipal | 9617 | 133310 | 9562 | 7133 | 112336 | 1960 | 16444 | 476055 | 5 | . | . | . | 33194 | 721701 | 11527 | Rural
Portland General Electric CompanyOR | 15248 | 2012 | Portland General Electric Company | Bundle | Private | OR | OR | Investor Owned | 804945 | 7505404 | 723440 | 601992 | 6883172 | 100187 | 216166 | 3547693 | 3339 | 714 | 8166 | 3 | 1623817 | 17944435 | 826969
Portland General Electric CompanyOR | 15248 | 2012 | Portland General Electric Company | Delivery | Private | OR | OR | Investor Owned | 0 | 0 | 0 | 16504 | 438470 | 452 | 16771 | 808238 | 46 | 0 | 0 | 0 | 33275 | 1246708 | 498
Powder River Energy CorporationMT | 19156 | 2012 | Powder River Energy Corporation | Bundle | Public | EMT | MT | Cooperative | 45.7 | 532 | 44 | 1817.1 | 13020 | 175 | 5465.5 | 96387 | 64 | . | . | . | 7328.3 | 109939 | 283 | Rural
PPL EnergyPlus LLCMT | 28802 | 2012 | PPL EnergyPlus LLC | Energy | Unreg | WMT | MT | Power Marketer | 0 | 0 | 0 | 3058.9 | 86404 | 4 | 73869.6 | 2128598 | 10 | 0 | 0 | 0 | 76928.5 | 2215002 | 14
Public Utility District No 1WA | 15327 | 2012 | Public Utility District No 1 | Bundle | Public | WA | WA | Political Subdivision | 2521.5517 | 30472.0617 | 1938.691 | 871.4483 | 10611.9383 | 461.309 | 0 | 0 | 0 | 0 | 0 | 0 | 3393 | 41084 | 2400 | Rural
PUD No 1 of Asotin CountyWA | 14771 | 2012 | PUD No 1 of Asotin County | Bundle | Public | WA | WA | Municipal | 0 | 0 | 0 | 14 | 282 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 282 | 3 | Rural
PUD No 1 of Benton CountyWA | 1579 | 2012 | PUD No 1 of Benton County | Bundle | Public | WA | WA | Political Subdivision | 50678 | 668018 | 40645 | 33237 | 520945 | 7341 | 22040 | 456313 | 724 | . | . | . | 105955 | 1645276 | 48710 | Urban
PUD No 1 of Chelan CountyWA | 3413 | 2012 | PUD No 1 of Chelan County | Bundle | Public | WA | WA | Political Subdivision | 24520.2 | 762266 | 36057 | 16161.1 | 469223 | 10333 | 6789.1 | 310897 | 1521 | 0 | 0 | 0 | 47470.4 | 1542386 | 47911 | Urban
PUD No 1 of Clallam CountyWA | 3644 | 2012 | PUD No 1 of Clallam County | Bundle | Public | WA | WA | Political Subdivision | 36111 | 446567 | 27183 | 11587 | 172056 | 3282 | 1750 | 28879 | 5 | . | . | . | 49448 | 647502 | 30470 | Rural
PUD No 1 of Clark CountyWA | 3660 | 2012 | PUD No 1 of Clark County | Bundle | Public | WA | WA | Political Subdivision | 212704 | 2317528 | 170221 | 97711 | 1296346 | 16331 | 41257 | 740918 | 25 | 0 | 0 | 0 | 351672 | 4354792 | 186577 | Urban
PUD No 1 of Cowlitz CountyWA | 4442 | 2012 | PUD No 1 of Cowlitz County | Bundle | Public | WA | WA | Political Subdivision | 55001 | 754607 | 43135 | 31685 | 381027 | 5058 | 153459 | 4015094 | 113 | . | . | . | 240145 | 5150728 | 48306 | Urban
PUD No 1 of Douglas CountyWA | 5326 | 2012 | PUD No 1 of Douglas County | Bundle | Public | WA | WA | Political Subdivision | 10371 | 392981 | 13893 | 4917 | 254538 | 1088 | 2499 | 104578 | 299 | . | . | . | 17787 | 752097 | 15280 | Rural
PUD No 1 of Ferry CountyWA | 6297 | 2012 | PUD No 1 of Ferry County | Bundle | Public | WA | WA | Political Subdivision | 3609.5 | 38511 | 2829 | 893.8 | 9664 | 489 | 3044.8 | 54878 | 25 | 0 | 0 | 0 | 7548.1 | 103053 | 3343 | Rural
PUD No 1 of Franklin CountyWA | 6716 | 2012 | PUD No 1 of Franklin County | Bundle | Public | WA | WA | Political Subdivision | 27963 | 336205 | 21997 | 21549 | 364908 | 1830 | 15220 | 284551 | 421 | . | . | . | 64732 | 985664 | 24248 | Rural
PUD No 1 of Grays Harbor CntyWA | 7548 | 2012 | PUD No 1 of Grays Harbor Cnty | Bundle | Public | WA | WA | Political Subdivision | 42555 | 497856 | 34660 | 24268 | 301746 | 4229 | 10355 | 176342 | 2524 | . | . | . | 77178 | 975944 | 41413 | Urban
PUD No 1 of Kittitas CountyWA | 10326 | 2012 | PUD No 1 of Kittitas County | Bundle | Public | WA | WA | Political Subdivision | 5468.5515 | 56179.8244 | 3503.0763 | 1994.2722 | 29453.6382 | 297.647 | 594.1763 | 6812.5374 | 388.2767 | 0 | 0 | 0 | 8057 | 92446 | 4189 | Rural
PUD No 1 of Klickitat CountyWA | 10393 | 2012 | PUD No 1 of Klickitat County | Bundle | Public | WA | WA | Political Subdivision | 12205.6 | 139822 | 10075 | 7113.3 | 98078 | 1883 | 3881.2 | 78032 | 245 | 0 | . | . | 23200.1 | 315932 | 12203 | Rural
PUD No 1 of Lewis CountyWA | 10944 | 2012 | PUD No 1 of Lewis County | Bundle | Public | WA | WA | Political Subdivision | 28977 | 457085 | 25707 | 12569 | 217839 | 5266 | 12144 | 249638 | 74 | . | . | . | 53690 | 924562 | 31047 | Rural
PUD No 1 of Mason CountyWA | 22355 | 2012 | PUD No 1 of Mason County | Bundle | Public | WA | WA | Political Subdivision | 5287.5171 | 59327.5739 | 4657.3341 | 1493.5829 | 15933.4261 | 454.6659 | 0 | 0 | 0 | 0 | 0 | 0 | 6781.1 | 75261 | 5112 | Rural
PUD No 1 of Okanogan CountyWA | 14055 | 2012 | PUD No 1 of Okanogan County | Bundle | Public | WA | WA | Political Subdivision | 18862.7 | 289640 | 16937 | 15590.4 | 270703 | 3738 | 1135.3 | 20584 | 4 | . | . | . | 35588.4 | 580927 | 20679 | Rural
PUD No 1 of Pend Oreille CntyWA | 14653 | 2012 | PUD No 1 of Pend Oreille Cnty | Bundle | Public | WA | WA | Political Subdivision | 8460 | 138253 | 7893 | 2489 | 49850 | 876 | 32048 | 814788 | 8 | . | . | . | 42997 | 1002891 | 8777 | Rural
PUD No 1 of Skamania CoWA | 17279 | 2012 | PUD No 1 of Skamania Co | Bundle | Public | WA | WA | Political Subdivision | 5480 | 74327 | 5223 | 1395.1 | 21912 | 563 | 1525.2 | 26953 | 55 | . | . | . | 8400.3 | 123192 | 5841 | Rural
PUD No 1 of Whatcom CountyWA | 40456 | 2012 | PUD No 1 of Whatcom County | Bundle | Public | WA | WA | Political Subdivision | . | . | . | . | 0 | . | 8870.3 | 195272 | 1 | . | . | . | 8870.3 | 195272 | 1
PUD No 2 of Grant CountyWA | 14624 | 2012 | PUD No 2 of Grant County | Bundle | Public | WA | WA | Political Subdivision | 35898 | 739941 | 35547 | 26925 | 720162 | 6406 | 81087 | 2469920 | 4649 | . | . | . | 143910 | 3930023 | 46602 | Urban
PUD No 3 of Mason CountyWA | 15419 | 2012 | PUD No 3 of Mason County | Bundle | Public | WA | WA | Political Subdivision | 32336.2 | 425976 | 30001 | 12847.8 | 185203 | 2247 | 2468.1 | 52358 | 1 | . | . | . | 47652.1 | 663537 | 32249 | Rural
Puget Sound Energy IncWA | 15500 | 2012 | Puget Sound Energy Inc | Bundle | Private | WA | WA | Investor Owned | 1126311.4 | 10869292 | 961914 | 865883.9 | 9081941 | 123756 | 107591 | 1183241 | 3600 | 307.1 | 3694 | 1 | 2100093.4 | 21138168 | 1089271 | 0
Puget Sound Energy IncWA | 15500 | 2012 | Puget Sound Energy Inc | Delivery | Private | WA | WA | Investor Owned | 0 | 0 | 0 | 591 | 76180 | 1 | 9145.3 | 1904693 | 15 | . | . | . | 9736.3 | 1980873 | 16 | 0
Raft River Rural Elec Coop IncID | 22814 | 2012 | Raft River Rural Elec Coop Inc | Bundle | Public | ID | ID | Cooperative | 1817 | 22408 | 1280 | 1872 | 38124 | 320 | 7074 | 156439 | 894 | 0 | 0 | 0 | 10763 | 216971 | 2494 | Rural
Ravalli County Elec Coop, IncMT | 26916 | 2012 | Ravalli County Elec Coop, Inc | Bundle | Public | WMT | MT | Cooperative | 11060 | 130987 | 9416 | 759 | 9461 | 377 | 173 | 2743 | 1 | 0 | 0 | 0 | 11992 | 143191 | 9794 | Rural
Riverside Electric CooperativeID | 56536 | 2012 | Riverside Electric Cooperative | Bundle | Public | ID | ID | Cooperative | 1238 | 20000 | 540 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1238 | 20000 | 540 | Rural
Rupert City ofID | 16416 | 2012 | Rupert City of | Bundle | Public | ID | ID | Municipal | 1948 | 36354 | 2380 | 940 | 24800 | 232 | 479 | 11920 | 1 | . | . | . | 3367 | 73074 | 2613 | Rural
Salem ElectricOR | 16555 | 2012 | Salem Electric | Bundle | Public | OR | OR | Cooperative | 15075 | 183577 | 16500 | 7877 | 102690 | 2068 | 1661 | 25806 | 10 | . | . | . | 24613 | 312073 | 18578 | Urban
Salmon River Electric Coop IncID | 16565 | 2012 | Salmon River Electric Coop Inc | Bundle | Public | ID | ID | Cooperative | 2600 | 32666 | 2142 | 1351 | 19882 | 437 | 7570 | 225195 | 115 | . | . | . | 11521 | 277743 | 2694 | Rural
Seattle City ofWA | 16868 | 2012 | Seattle City of | Bundle | Public | WA | WA | Municipal | 243806 | 3146951 | 362524 | 356093 | 5237477 | 39866 | 64316 | 1081568 | 214 | 48 | 646 | 4 | 664263 | 9466642 | 402608 | Urban
Shell Energy North America (US), L.P.WA | 4410 | 2012 | Shell Energy North America (US), L.P. | Energy | Unreg | WA | WA | Power Marketer | 0 | 0 | 0 | 0 | 0 | 0 | 13387.1 | 604899 | 2 | 0 | 0 | 0 | 13387.1 | 604899 | 2
Sheridan Electric Coop, IncMT | 16759 | 2012 | Sheridan Electric Coop, Inc | Bundle | Public | EMT | MT | Cooperative | 2950 | 34059 | 2729 | 7448.1 | 67399 | 781 | 606.3 | 4435 | 614 | . | . | . | 11004.4 | 105893 | 4124 | Rural
Sierra Pacific Industries IncWA | 17164 | 2012 | Sierra Pacific Industries Inc | Bundle | Unreg | WA | WA | Power Marketer | . | . | . | . | 0 | . | 3553 | 37537 | 1 | . | . | . | 3553 | 37537 | 1
Snohomish County PUD No 1WA | 17470 | 2012 | Snohomish County PUD No 1 | Bundle | Public | WA | WA | Political Subdivision | 297937 | 3531333 | 295622 | 178463 | 2364872 | 30149 | 40632 | 639379 | 78 | . | . | . | 517032 | 6535584 | 325849 | Urban
South Side Electric, IncID | 17576 | 2012 | South Side Electric, Inc | Bundle | Public | ID | ID | Cooperative | 1525.1507 | 27737.648 | 917.7276 | 0 | 0 | 0 | 1093.8493 | 29768.352 | 313.2724 | 0 | 0 | 0 | 2619 | 57506 | 1231 | Rural
Southeast Electric Coop, IncMT | 17593 | 2012 | Southeast Electric Coop, Inc | Bundle | Public | EMT | MT | Cooperative | 2338.7897 | 16224.6929 | 1940.202 | 92.5727 | 791.4733 | 17.8182 | 907.6377 | 9264.8338 | 1.9798 | 0 | 0 | 0 | 3339 | 26281 | 1960 | Rural
Sun River Electric Coop, IncMT | 18401 | 2012 | Sun River Electric Coop, Inc | Bundle | Public | EMT | MT | Cooperative | 5660.2 | 45248 | 4435 | 1318.2 | 15275 | 285 | 3009.3 | 28919 | 890 | . | . | . | 9987.7 | 89442 | 5610 | Rural
Surprise Valley Electrification Corp.OR | 18260 | 2012 | Surprise Valley Electrification Corp. | Bundle | Public | OR | OR | Cooperative | 1161.9 | 15827 | 1148 | 297 | 3872 | 365 | 984.2 | 15105 | 250 | 0 | 0 | 0 | 2443.1 | 34804 | 1763 | Rural
Tacoma City ofWA | 18429 | 2012 | Tacoma City of | Bundle | Public | WA | WA | Municipal | 142439.2 | 1898579 | 151174 | 23499.7 | 334921 | 15086 | 122250 | 2505933 | 2757 | 207.1 | 2632 | 1 | 288396 | 4742065 | 169018 | Urban
Tanner Electric CoopWA | 18448 | 2012 | Tanner Electric Coop | Bundle | Public | WA | WA | Cooperative | 6312.8 | 56449 | 4268 | 2877.8 | 35279 | 290 | . | 0 | . | . | . | . | 9190.6 | 91728 | 4558 | Rural
Tillamook Peoples Utility DistOR | 18917 | 2012 | Tillamook Peoples Utility Dist | Bundle | Public | OR | OR | Political Subdivision | 19170 | 229065 | 18433 | 8535 | 122911 | 2147 | 5273 | 108791 | 5 | . | . | . | 32978 | 460767 | 20585 | Urban
Tongue River Electric Coop IncMT | 19022 | 2012 | Tongue River Electric Coop Inc | Bundle | Public | EMT | MT | Cooperative | 7360 | 51389 | 4258 | 1531 | 12602 | 527 | 2503 | 19184 | 148 | . | . | . | 11394 | 83175 | 4933 | Rural
Town of EatonvilleWA | 5631 | 2012 | Town of Eatonville | Bundle | Public | WA | WA | Municipal | 1023.856 | 15557.9615 | 973.1588 | 828.144 | 12187.0385 | 196.8412 | 0 | 0 | 0 | 0 | 0 | 0 | 1852 | 27745 | 1170 | Rural
Town of RustonWA | 16462 | 2012 | Town of Ruston | Bundle | Public | WA | WA | Municipal | 506 | 6216 | 489 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 506 | 6216 | 489 | Rural
Town of SteilacoomWA | 18051 | 2012 | Town of Steilacoom | Bundle | Public | WA | WA | Municipal | 2166.8 | 30911 | 2701 | 459.2 | 7376 | 162 | . | 0 | . | . | . | . | 2626 | 38287 | 2863 | Rural
Umatilla Electric Coop AssnOR | 19325 | 2012 | Umatilla Electric Coop Assn | Bundle | Public | OR | OR | Cooperative | 12794.8 | 164377 | 10961 | 10359.7 | 167374 | 1859 | 30618.2 | 641630 | 1434 | . | . | . | 53772.7 | 973381 | 14254 | Rural
United Electric Co-op, IncID | 19502 | 2012 | United Electric Co-op, Inc | Bundle | Public | ID | ID | Cooperative | 5635 | 86074 | 4176 | 2774 | 45738 | 935 | 5780 | 126888 | 1057 | . | . | . | 14189 | 258700 | 6168 | Rural
USBIA-Mission Valley PowerMT | 19603 | 2012 | USBIA-Mission Valley Power | Bundle | Public | WMT | MT | Federal | 14491 | 217040 | 14512 | 7359 | 121085 | 5339 | 1046 | 15177 | 1042 | 0 | 0 | 0 | 22896 | 353302 | 20893 | Rural
Vera Irrigation District #15WA | 19784 | 2012 | Vera Irrigation District #15 | Bundle | Public | WA | WA | Political Subdivision | 8547 | 136247 | 9184 | 5219 | 84015 | 992 | . | 0 | . | . | . | . | 13766 | 220262 | 10176 | Rural
Vigilante Electric Coop, IncID | 23586 | 2012 | Vigilante Electric Coop, Inc | Bundle | Public | ID | ID | Cooperative | 14.2 | 100 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.2 | 100 | 33 | Rural
Vigilante Electric Coop, IncMT | 23586 | 2012 | Vigilante Electric Coop, Inc | Bundle | Public | WMT | MT | Cooperative | 7462.2 | 94838 | 7809 | 4188.2 | 65735 | 1303 | . | 0 | . | . | . | . | 11650.4 | 160573 | 9112 | Rural
Wasco Electric Coop, IncOR | 20138 | 2012 | Wasco Electric Coop, Inc | Bundle | Public | OR | OR | Cooperative | 4711 | 49264 | 3769 | 1545 | 15986 | 533 | 3107 | 42057 | 331 | . | . | . | 9363 | 107307 | 4633 | Rural
West Oregon Electric Coop IncOR | 20385 | 2012 | West Oregon Electric Coop Inc | Bundle | Public | OR | OR | Cooperative | 7202.0619 | 53372.2872 | 3922.7833 | 711.3655 | 5319.0651 | 278.7865 | 1049.5725 | 9503.6477 | 49.4302 | 0 | 0 | 0 | 8963 | 68195 | 4251 | Rural
Western Area Power AdministrationMT | 27000 | 2012 | Western Area Power Administration | Bundle | Public | EMT | MT | Federal | . | . | . | 2402 | 105218 | 22 | . | 0 | . | . | . | . | 2402 | 105218 | 22
Yellowstone Valley Elec Co-opMT | 20997 | 2012 | Yellowstone Valley Elec Co-op | Bundle | Public | EMT | MT | Cooperative | 23304 | 185958 | 15863 | 6080 | 52012 | 1444 | 978 | 8869 | 187 | . | . | . | 30362 | 246839 | 17494 | Rural

## 2005 Sales Source Data
2005 Regional Sales Numbers
Source: "RegionWideSubstations" sheet of DE-Distribution-7P_V4 Modifications: None Purpose: Represents 2005 sales and is used to duplicate 7P approach of calculating number of substations in 2012 based on load growth in leiu of more detailed data from utilities which was not available during 7P development. There are some duplicates in here (e.g. PacifiCorp) so the PivotTable approach is still needed to get gross total sales info.
1 | 2 | 3 | 4 | 5 | 6 | 6 | 7 | 8 | 9 | 10
UTILITY_NAME | Residential Sales (MWh) | Commercial Energy MWh | Industrial/Other MWh | Dummy Column - Only used to keep column numbers consistent between "20XX Sales" Sheets | Annual Energy MWh | Annual Energy MWh | Residential Consumers (n) | Commercial Consumers | Industrial/Other Consumers | Total Number of Customers
Puget Sound Energy Inc | 10722240 | 8917680 | 1480440 | 0 | 23183514 | 23183514 | 1039523 | 114840 | 6574 | 1160937
Portland General Electric Company | 7322964 | 7075000 | 4474000 | 0 | 18432528 | 18432528 | 680093 |  |  | 680093
PacifiCorp | 5374487 | 6000000 | 2125513 | 0 | 13500000 | 13500000 | 447272 |  |  | 447272
Avista Corp | 3419532 | 4459916 | 4459916 | 0 | 12339364 | 12339364 | 294036 |  |  | 294036
Idaho Power Co | 4760275 | 3582126.3588 | 3582126.3588 | 0 | 11924527.7176 | 11924527.7176 | 373603 |  |  | 373603
Seattle City of | 2948779 | 5533365.9469 | 679321.0531 | 0 | 9161466 | 9161466 | 336363 | 39261 | 241 | 375865
NorthWestern Corporation | 567652.86 | 3225689.07 | 3225689.07 | 0 | 7019031 | 7019031 | 68294.88 |  |  | 68294.88
Snohomish County PUD No 1 | 3188146 | 2950413.3322 | 166616.6678 | 0 | 6305176 | 6305176 | 272829 | 27270 | 77 | 300176
Tacoma City of | 1760110 | 644695.9982 | 2217847.0018 | 0 | 4622653 | 4622653 | 145375 | 15011 | 2582 | 162968
PacifiCorp | 2630213 | 934893.5 | 934893.5 | 0 | 4500000 | 4500000 | 185032 |  |  | 185032
PUD No 1 of Cowlitz County | 725791 | 2743381.549 | 915688.451 | 0 | 4384861 | 4384861 | 41402 | 5213 | 87 | 46702
PUD No 1 of Clark County | 2230688 | 1984336.2823 | 74604.7177 | 0 | 4289629 | 4289629 | 160224 | 13299 | 25 | 173548
PUD No 2 of Grant County | 669081 | 141591.6864 | 2207938.3136 | 0 | 3018611 | 3018611 | 31665 | 5651 | 4406 | 41722
Eugene City of | 960623 | 1687272.9204 | 15278.0796 | 0 | 2663174 | 2663174 | 75298 | 8835 | 4 | 84137
PUD No 1 of Benton County | 622639 | 311006.9418 | 668862.0582 | 0 | 1602508 | 1602508 | 36963 | 6705 | 721 | 44389
PUD No 1 of Chelan County | 665318 | 174800.118 | 582977.882 | 0 | 1423096 | 1423096 | 32769 | 9373 | 1563 | 43705
Flathead Electric Coop Inc | 568902 | 107394.6104 | 704064.3896 | 0 | 1380361 | 1380361 | 49172 | 1083 | 355 | 50610
Central Lincoln People's Ut Dt | 414445 | 543847.6325 | 334076.3675 | 0 | 1292369 | 1292369 | 31371 | 5307 | 163 | 36841
PUD No 1 of Grays Harbor Cnty | 486892 | 260459 | 245479 | 0 | 992830 | 992830 | 34096 | 6919 | 44 | 41059
Clatskanie Peoples Util Dist | 67769 | 794740.6452 | 117739.3548 | 0 | 980249 | 980249 | 3864 | 540 | 4 | 4408
PUD No 1 of Pend Oreille Cnty | 131586 | 723974.5072 | 121530.4928 | 0 | 977091 | 977091 | 7408 | 834 | 7 | 8249
McMinnville City of | 192092 | 549580.4591 | 83244.5409 | 0 | 824917 | 824917 | 12092 | 3301 | 25 | 15418
PUD No 1 of Franklin County | 275018 | 526516.1462 | 8893.8538 | 0 | 810428 | 810428 | 18963 | 4736 | 4 | 23703
PUD No 1 of Lewis County | 395293 | 312370.7685 | 100617.2315 | 0 | 808281 | 808281 | 23979 | 4781 | 77 | 28837
City of Springfield | 382311 | 374423.3882 | 26482.6118 | 0 | 783217 | 783217 | 27085 | 3676 | 13 | 30774
City of Richland | 295048 | 424367.4966 | 33365.5034 | 0 | 752781 | 752781 | 18977 | 2035 | 8 | 21020
Port Angeles City of | 130727 | 511642.9882 | 23034.0118 | 0 | 665404 | 665404 | 8662 | 1777 | 4 | 10443
Idaho Falls City of | 272395 | 362359.1154 | 16340.8846 | 0 | 651095 | 651095 | 20721 | 3548 | 8 | 24277
PUD No 3 of Mason County | 369780 | 246247.5157 | 2228.4843 | 0 | 618256 | 618256 | 28619 | 2210 | 1 | 30830
Consumers Power, Inc | 251024 | 24875.245 | 341268.755 | 0 | 617168 | 617168 | 18587 | 812 | 557 | 19956
Umatilla Electric Coop Assn | 153858 | 401524.4952 | 42521.5048 | 0 | 597904 | 597904 | 10285 | 1322 | 7 | 11614
PUD No 1 of Clallam County | 402235 | 52933.0912 | 140737.9088 | 0 | 595906 | 595906 | 25376 | 2708 | 360 | 28444
PUD No 1 of Douglas County | 338778 | 25197.4307 | 186588.5693 | 0 | 550564 | 550564 | 14766 | 1580 | 585 | 16931
Columbia River Peoples Ut Dist | 188505 | 189105.8081 | 110588.1919 | 0 | 488199 | 488199 | 15254 | 2394 | 70 | 17718
Inland Power & Light Company | 545226 |  |  | 0 | 473000 | 473000 | 31987 | 897 | 51 | 32935
Emerald People's Utility Dist | 251360 | 176829.539 | 15802.461 | 0 | 443992 | 443992 | 16274 | 2238 | 10 | 18522
Big Bend Electric Coop, Inc | 90453 | 3508.7517 | 309322.2483 | 0 | 403284 | 403284 | 4094 | 483 | 2129 | 6706
Tillamook Peoples Utility Dist | 208751 | 186282.0573 | 7150.9427 | 0 | 402184 | 402184 | 17120 | 2084 | 4 | 19208
Central Electric Coop Inc | 400482 |  |  | 0 | 398735 | 398735 | 24585 | 1260 | 1380 | 27225
Peninsula Light Company | 386574 |  |  | 0 | 386574 | 386574 | 25787 |  |  | 25787
Benton Rural Electric Assn | 207909 | 110838.4255 | 11682.5745 | 0 | 330430 | 330430 | 11292 | 759 | 4 | 12055
Lower Valley Energy Inc | 329905 |  |  | 0 | 329905 | 329905 | 18097 |  |  | 18097
Coos-Curry Electric Coop, Inc | 182058 | 102562 | 0 | 0 | 284620 | 284620 | 14390 | 2066 |  | 16456
PUD No 1 of Klickitat County | 119451 | 157838.1366 | 4960.8634 | 0 | 282250 | 282250 | 9244 | 1909 | 3 | 11156
Pacific Public Utility District No 2 | 165674 | 113245.279 | 2138.721 | 0 | 281058 | 281058 | 14367 | 2118 | 2 | 16487
Salmon River Electric Coop Inc | 26881 | 245171.0558 | 13851.4721 | 0 | 272874 | 272874 | 1951 | 354 | 2 | 2307
Midstate Electric Coop, Inc | 208436 | 7811.5506 | 43234.4494 | 0 | 259482 | 259482 | 15141 | 1384 | 383 | 16908
City of Forest Grove | 105163 | 46640.8136 | 98191.1864 | 0 | 249995 | 249995 | 7596 | 1045 | 110 | 8751
Oregon Trail El Cons Coop, Inc | 246248 |  |  | 0 | 246248 | 246248 | 24046 |  |  | 24046
Northern Wasco County PUD | 130575 | 10997.6355 | 100856.3645 | 0 | 242429 | 242429 | 8888 | 410 | 188 | 9486
Kootenai Electric Coop Inc | 243294 |  |  | 0 | 233093 | 233093 | 18702 | 876 | 87 | 19665
City of Centralia | 112752 | 116584 | 0 | 0 | 229336 | 229336 | 8037 | 1543 |  | 9580
Harney Electric Coop, Inc | 27821 | 1477.6204 | 96523.6898 | 0 | 222346 | 222346 | 1528 | 139 | 908 | 2575
PUD No 1 of Okanogan County | 262901 |  |  | 0 | 216486 | 216486 | 15759 | 3620 | 3 | 19382
Elmhurst Mutual Power & Light Co | 211302 |  |  | 0 | 211302 | 211302 | 12699 |  |  | 12699
PUD No 1 of Whatcom County | 0 |  | 207228 | 0 | 207228 | 207228 | 0 |  | 1 | 1
Lane Electric Coop Inc | 184786 | 9567.8638 | 8467.1362 | 0 | 202821 | 202821 | 11597 | 565 | 25 | 12187
Vera Irrigation District #15 | 124864 | 76174 | 0 | 0 | 201038 | 201038 | 8350 | 843 |  | 9193
Raft River Rural Elec Coop Inc | 36000 | 2332.2489 | 80422.3756 | 0 | 199177 | 199177 | 2982 | 232 | 800 | 4014
Northern Lights, Inc | 180512 | 8588.9281 | 8472.0719 | 0 | 197573 | 197573 | 15903 | 588 | 29 | 16520
USBIA-Mission Valley Power | 194681 |  |  | 0 | 194681 | 194681 | 13609 |  |  | 13609
Columbia Rural Elec Assn, Inc | 43104 | 6599.331 | 70429.8345 | 0 | 190563 | 190563 | 2508 | 476 | 508 | 3492
City of Ellensburg | 59644 | 128482.4236 | 1818.5764 | 0 | 189945 | 189945 | 7008 | 1413 | 1 | 8422
Salem Electric | 176428 |  |  | 0 | 176428 | 176428 | 15460 |  |  | 15460
Fall River Rural Elec Coop Inc | 116956 | 8189.0455 | 49252.9545 | 0 | 174398 | 174398 | 10451 | 1656 | 498 | 12605
City of Ashland | 87675 | 81481 | 0 | 0 | 169156 | 169156 | 9264 | 2046 |  | 11310
Clearwater Power Company | 111456 | 12046.0155 | 33657.9845 | 0 | 157160 | 157160 | 8979 | 680 | 95 | 9754
Canby Utility Board | 73142 | 62332.9089 | 18731.0911 | 0 | 154206 | 154206 | 5639 | 599 | 9 | 6247
Glacier Electric Coop, Inc | 61272 | 23817.3906 | 59706.6094 | 0 | 144796 | 144796 | 5495 | 1460 | 183 | 7138
Lakeview Light & Power | 138820 |  |  | 0 | 138820 | 138820 | 7806 |  |  | 7806
Orcas Power & Light Coop | 131805 | 6402.6247 | 523.3753 | 0 | 138731 | 138731 | 11070 | 1468 | 6 | 12544
Blachly-Lane Cnty Coop El Assn | 51101 | 45837.1867 | 19551.4066 | 0 | 136041 | 136041 | 3163 | 211 | 9 | 3383
Missoula Electric Coop, Inc | 135638 |  |  | 0 | 135638 | 135638 | 11681 |  |  | 11681
PUD No 1 of Skamania Co | 67302 | 23089.5131 | 16283.7434 | 0 | 122959 | 122959 | 4956 | 553 | 39 | 5548
Douglas Electric Coop, Inc | 113405 | 545.6379 | 4998.3621 | 0 | 118949 | 118949 | 8570 | 548 | 251 | 9369
Ravalli County Elec Coop, Inc | 115686 |  |  | 0 | 115686 | 115686 | 8927 |  |  | 8927
City of Cheney | 42997 | 54288.6364 | 17372.3636 | 0 | 114658 | 114658 | 3748 | 500 | 8 | 4256
City of Milton-Freewater | 59932 | 24920.3911 | 25016.6089 | 0 | 109869 | 109869 | 3494 | 1295 | 65 | 4854
City of Hermiston | 49525 | 55502 | 0 | 0 | 105027 | 105027 | 4382 | 783 |  | 5165
Lincoln Electric Coop, Inc | 61753 | 1242.8445 | 39186.1555 | 0 | 102182 | 102182 | 3975 | 170 | 268 | 4413
City of Burley | 42664 | 55034 | 0 | 0 | 97698 | 97698 | 3653 | 656 |  | 4309
Columbia Basin Elec Cooperative, Inc | 37000 | 4923.7388 | 26901.6306 | 0 | 95727 | 95727 | 3038 | 399 | 218 | 3655
Modern Electric Water Company | 89999 |  |  | 0 | 89999 | 89999 | 7942 |  |  | 7942
United Electric Co-op, Inc | 83316 | 0 | 0 | 0 | 83316 | 83316 | 3927 | 224 | 924 | 5075
PUD No 1 of Ferry County | 32911 | 8967.2297 | 20399.3851 | 0 | 82677 | 82677 | 2703 | 422 | 96 | 3221
Vigilante Electric Coop, Inc | 79323 |  |  | 0 | 79323 | 79323 | 7057 |  |  | 7057
Rupert City of | 36280 | 40862 | 0 | 0 | 77142 | 77142 | 2337 | 392 |  | 2729
Wasco Electric Coop, Inc | 46912 | 262.5589 | 26236.4411 | 0 | 73411 | 73411 | 3684 | 270 | 1349 | 5303
City of Bonners Ferry | 23131 | 27276.6808 | 10046.6596 | 0 | 70501 | 70501 | 1815 | 543 | 20 | 2378
Ohop Mutual Light Company, Inc | 69585 |  |  | 0 | 69585 | 69585 | 3851 |  |  | 3851
City of Blaine | 21123 | 28271.0339 | 7248.9831 | 0 | 63892 | 63892 | 2241 | 507 | 13 | 2761
PUD No 1 of Kittitas County | 44314 | 1515.3826 | 16013.6174 | 0 | 61843 | 61843 | 3259 | 282 | 149 | 3690
PUD No 1 of Mason County | 47960 | 13865 | 0 | 0 | 61825 | 61825 | 4501 | 430 |  | 4931
West Oregon Electric Coop Inc | 49161 | 5850.9083 | 6182.0917 | 0 | 61194 | 61194 | 3938 | 265 | 14 | 4217
City of Bandon | 31794 | 23209.2976 | 1753.8512 | 0 | 58511 | 58511 | 2731 | 397 | 3 | 3131
City of Milton | 39390 | 18280 | 0 | 0 | 57670 | 57670 | 3153 | 179 |  | 3332
City of Weiser | 24636 | 29715.398 | 798.801 | 0 | 55949 | 55949 | 2399 | 372 | 1 | 2772
City of Monmouth | 34470 | 2858.7002 | 18389.2998 | 0 | 55718 | 55718 | 3419 | 171 | 55 | 3645
City of Cashmere | 19327 | 17624.5714 | 18731.4286 | 0 | 55683 | 55683 | 950 | 207 | 11 | 1168
Parkland Light & Water Company | 52894 |  |  | 0 | 52894 | 52894 | 3866 |  |  | 3866
Lost River Electric Coop Inc | 25537 | 431.5364 | 12412.7318 | 0 | 50794 | 50794 | 1696 | 178 | 512 | 2386
Hood River Electric Coop | 47944 | 0 | 0 | 0 | 47944 | 47944 | 3078 | 214 | 197 | 3489
Surprise Valley Electrification Corp. | 46712 |  |  | 0 | 46712 | 46712 | 3763 |  |  | 3763
Wells Rural Electric Co | 45224 |  |  | 0 | 45224 | 45224 | 4037 |  |  | 4037
Tanner Electric Coop | 51533 |  |  | 0 | 41706 | 41706 | 3968 | 230 | 378 | 4576
City of McCleary | 12685 | 16662.0594 | 5462.9703 | 0 | 40273 | 40273 | 953 | 61 | 2 | 1016
Nespelem Valley Elec Coop, Inc | 17605 | 2068.7912 | 9257.6044 | 0 | 38189 | 38189 | 1500 | 219 | 98 | 1817
Town of Steilacoom | 30517 | 7216 | 0 | 0 | 37733 | 37733 | 2675 | 128 |  | 2803
Idaho Cnty L&P Coop Assn, Inc | 33231 | 1435.169 | 925.9155 | 0 | 36518 | 36518 | 3043 | 217 | 14 | 3274
PUD No 1 Wahkiakum County | 26264 | 9815 | 0 | 0 | 36079 | 36079 | 1920 | 342 |  | 2262
Okanogan County Elec Coop, Inc | 30797 | 0 | 0 | 0 | 30797 | 30797 | 2832 | 228 | 135 | 3195
City of Plummer | 9016 | 14488.5106 | 6791.4894 | 0 | 30296 | 30296 | 644 | 128 | 3 | 775
Heyburn City of | 16393 | 10266.2143 | 1115.8929 | 0 | 28891 | 28891 | 1089 | 92 | 1 | 1182
City of Sumas | 4002 | 7077.2958 | 16850.7042 | 0 | 27930 | 27930 | 454 | 126 | 15 | 595
South Side Electric, Inc | 24662 | 0 | 0 | 0 | 24662 | 24662 | 703 | 177 |  | 880
Town of Eatonville | 14697 | 9595 | 0 | 0 | 24292 | 24292 | 1475 | 107 |  | 1582
Columbia Power Coop Assn Inc | 13655 | 359.7509 | 4845.6245 | 0 | 23706 | 23706 | 1276 | 196 | 264 | 1736
City of Soda Springs | 12349 | 9570.9792 | 644.5104 | 0 | 23209 | 23209 | 1446 | 297 | 2 | 1745
City of Chewelah | 11017 | 10076 | 0 | 0 | 21093 | 21093 | 1080 | 185 |  | 1265
City of Drain | 7502 | 6208.9544 | 6758.0456 | 0 | 20469 | 20469 | 512 | 147 | 8 | 667
City of Cascade Locks | 8334 | 12005 | 0 | 0 | 20339 | 20339 | 501 | 68 |  | 569
City of Coulee Dam | 9810 | 8234 | 0 | 0 | 18044 | 18044 | 517 | 86 |  | 603
East End Mutual Elec Co Ltd | 13016 |  |  | 0 | 13016 | 13016 | 559 |  |  | 559
City of Troy | 9724 |  |  | 0 | 9724 | 9724 | 786 |  |  | 786
Town of Ruston | 5058 | 129 | 0 | 0 | 5187 | 5187 | 417 | 1 |  | 418
Alder Mutual Light Co, Inc | 3285 |  |  | 0 | 3285 | 3285 | 246 |  |  | 246
City of Albion | 1908 | 1054 | 0 | 0 | 2962 | 2962 | 120 | 19 |  | 139
City of Declo | 1257 | 78.3636 | 783.6364 | 0 | 2119 | 2119 | 101 | 20 | 10 | 131
Farmers Electric Company, Ltd | 1892 |  |  | 0 | 1892 | 1892 | 99 |  |  | 99
City of Minidoka | 473 | 93 | 0 | 0 | 566 | 566 | 41 | 2 |  | 43