## Cover_page
Appendix B: Capital Construction Costs for Summer/ Fall Chinook Program
Appendix B: Capital Construction Costs for Spring Chinook Program

## App_B_Construction_Costs
Project: Chief Joseph Dam Fish Hatchery |  |  |  | Date: | 4/15/2004-5pm
|  |  |  | Type of Estimate: | Conceptual Design
LINE ITEM | DESCRIPTION |  |  | QTY | UNIT | UNIT PRICE | COST
COE water systems for hatchery rearing shown in line item 169
Piping based upon COE termination at 10 feet from headbox.
1 | 30" diam, HDPE, Tunnel water to headbox |  |  | 40 | lf | 135 | 5400
2 | 36" diam, HDPE, Reservoir water to headbox |  |  | 40 | lf | 155 | 6200
3 | 36"Butterfly valve on reservoir water at headbox w/electrical controls |  |  | 1 | ea | 10000 | 10000
4 | 36" diam, HDPE overflow to 48" drain |  |  | 250 | lf | 155 | 38750
|  |  |  | Total to headbox |  |  | 60350 | 60350
Headbox with drum filter on Reservoir supply
5 | Concrete footings, 12" |  |  | 40 | cy | 300 | 12000
6 | Concrete slab on grade, 6" |  |  | 8 | cy | 300 | 2400
7 | Concrete slab, 2nd level, 8" |  |  | 24 | cy | 400 | 9600
8 | Concrete exterior walls, 9" |  |  | 240 | cy | 500 | 120000
9 | Concrete weir walls, 9" |  |  | 30 | cy | 400 | 12000
10 | Grating, fiberglass |  |  | 304 | sf | 7 | 2128
11 | Drum Filter system |  |  | 1 | ls | 500000 | 500000
12 | Stairs, galv steel, 4' wide, 50 risers |  |  | 50 | risers | 225 | 11250
13 | Landings, 4x4 |  |  | 2 | ea | 600 | 1200
14 | Doors, metal, 36x78, with hardware |  |  | 2 | ea | 350 | 700
15 | Roof, Metal |  |  | 650 | sf | 10 | 6500
16 | Louvers, SS, 36x36 |  |  | 2 | ea | 400 | 800
|  |  |  | Total for headbox |  |  | 678578
Piping from headbox to S/F raceways
17 | 36" diam, HDPE, Reservoir water |  |  | 660 | lf | 155 | 102300
18 | 30" diam, HDPE, Well water |  |  | 660 | lf | 135 | 89100
19 | 36" various fittings |  |  | 1 | ls | 25000 | 25000
20 | 30" various fittings |  |  | 1 | ls | 20000 | 20000
21 | 24" flow meter |  |  | 2 | ea | 2500 | 5000
22 | 30" flow meter |  |  | 2 | ea | 3000 | 6000
23 | 24"x24" sluice gate at raceways |  |  | 4 | ea | 10000 | 40000
24 | 30"x30" sluice gate at raceways |  |  | 4 | ea | 12000 | 48000
|  |  |  | Total to raceways |  |  | 335400 | 335400
500cfs Pumped Fish Ladder Attraction Water
Vert turb pumps within screened 50wx40dx30h
structure beside entrance to fish ladder
25 | Concrete slabs, 12" |  |  | 120 | cy | 350 | 42000
26 | Concrete walls, 12" |  |  | 288 | cy | 500 | 144000
27 | (100cfs)45,000gpm/10'TDH, 150hp, 430rpm pump |  |  | 5 | ea | 25000 | 125000
Hydro-foil pump 48PL
28 | Inlet screen structure (1" ss rods @ 1.5" c-c) |  |  | 18200 | lb | 10 | 182000
29 | Sheet pile around excavation, drive & extract |  |  | 13000 | sf | 12 | 156000
30 | Excavation, 1cy clam shell, haul 1/2 mi |  |  | 4000 | cy | 10 | 40000
31 | Backfill and use for access road fill |  |  | 4000 | cy | 10 | 40000
32 | Rock armor replacement |  |  | 1 | ls | 20000 | 20000
33 | Access road to structure |  |  | 1 | ls | 10000 | 10000
34 | Electrical Panels and misc |  |  | 1 | ls | 20000 | 20000
35 | Gratings, fiberglass |  |  | 1700 | sf | 7 | 11900
36 | Structural steel |  |  | 8000 | lb | 10 | 80000
|  |  |  | Total for attraction water |  |  | 870900
Early S/F Chinook Raceways ( bank of 20 units)
37 | Concrete slabs, 6" |  |  | 384 | cy | 350 | 134400
38 | Concrete walls, 9" |  |  | 414 | cy | 400 | 165600
39 | Sluice gates, 36"x18", inlet, topping |  |  | 20 | ea | 3000 | 60000
40 | Stop logs, 3"x 6'x4' |  |  | 1440 | bf | 3 | 4320
41 | Flow distribution plate, SS, 1/4" |  |  | 633 | sf | 10 | 6330
42 | Screens, SS, 4 per raceway, var sizes, 50% redun. |  |  | 5400 | sf | 10 | 54000
43 | Grating, fiberglass, supply & drain channels |  |  | 1600 | sf | 7 | 11200
44 | Grating, fiberglass, center walls |  |  | 1680 | sf | 10 | 16800
45 | Feeders, demand, 2 per raceway |  |  | 40 | ea | 1200 | 48000
46 | Misc. metals, braces, hangers, channels |  |  | 1 | ls | 17000 | 17000
47 | 6" Raceway vacuum cleaning drain to connection w/ 6" from Late S/F |  |  | 375 | lf | 45 | 16875
|  |  |  | Total for Early S/F raceway bank |  |  | 534525
Late S/F Chinook Raceways ( bank of 24 units)
48 | Concrete slabs, 6" |  |  | 461 | cy | 350 | 161350
49 | Concrete walls, 9" |  |  | 496 | cy | 400 | 198400
50 | Sluice gates, 36"x18", inlet, topping |  |  | 24 | ea | 3000 | 72000
51 | Stop logs, 3"x 6'x4' |  |  | 1728 | bf | 3 | 5184
52 | Flow distribution plate, SS, 1/4" |  |  | 760 | sf | 10 | 7600
53 | Screens, SS, 4 per raceway, var sizes, 50% redun. |  |  | 6480 | sf | 10 | 64800
54 | Grating, fiberglass, supply & drain channels |  |  | 1920 | sf | 7 | 13440
55 | Grating, fiberglass, center walls |  |  | 2020 | sf | 10 | 20200
56 | Feeders, demand, 2 per raceway |  |  | 48 | ea | 1200 | 57600
57 | Misc. metals, braces, hangers, channels |  |  | 1 | ls | 17000 | 17000
58 | 6" Raceway vacuum cleaning drain to aeration/settling facility |  |  | 480 | lf | 45 | 21600
|  |  |  | Total for Late S/F raceway bank |  |  | 639174
Spawn House
59 | Building Area, Concrete lower walls w/ upper metal, roof at 6:12 slope |  |  | 1224 | sf | 60 | 73440
60 | Pumps for sorting tubes water supply |  |  | 1 | ea | 1000 | 1000
61 | Valves for fish sorting tubes |  |  | 1 | ls | 2000 | 2000
62 | Mechanical, plumbing/air compressor |  |  | 1 | ls | 2000 | 2000
63 | Electrical- pump controls/lighting/power |  |  | 1 | ls | 4000 | 4000
64 | Misc. equipment for anesthetic treatment |  |  | 1 | ls | 4000 | 4000
|  |  |  | Total for spawn house |  |  | 86440
Fish ladder and holding/sorting tanks
65 | Excavation w/1.5 cy hoe and haul 1 mile |  |  | 500 | cy | 8 | 4000
66 | Slab on grade and footings |  |  | 134 | cy | 300 | 40200
67 | Exterior walls, 9" |  |  | 460 | cy | 400 | 184000
68 | Weir walls, 9" |  |  | 33 | cy | 500 | 16500
69 | Backfill and compaction |  |  | 2150 | cy | 15 | 32250
70 | Grating cover |  |  | 1800 | sf | 10 | 18000
71 | Vehicle fish ladder crossing cover |  |  | 36 | ea | 600 | 21600
|  |  |  | Total for ladder and holding/sorting |  |  | 316550
Start tank building for S/F Chinook
72 | Footings, 12" |  |  | 50 | ls | 300 | 15000
73 | Slabs, 9" |  |  | 360 | ls | 350 | 126000
74 | Exterior walls, 9" |  |  | 200 | ls | 400 | 80000
75 | Ceiling/2nd floor beam/truss system |  |  | 12000 | sf | 15 | 180000
76 | Stairs, metal, 25 risers |  |  | 25 | risers | 225 | 5625
77 | Roof system |  |  | 12640 | sf | 10 | 126400
78 | Piping, four systems for supply, throughout building |  |  | 2 | systems | 75000 | 150000
79 | Piping, drain and fish transfer to raceways |  |  | 1 | ls | 20000 | 20000
80 | Lighting and power |  |  | 1 | ls | 20000 | 20000
81 | Start tanks, alum. 4X40X3deep |  |  | 40 | ea | 4000 | 160000
82 | 6" start tank vacuum drain to 6" line from Early S/F raceways |  |  | 600 | lf | 45 | 27000
83 | 36" drain pipe, HDPE, to Early S/F 48" raceway drain |  |  | 300 | lf | 155 | 46500
|  |  |  | Total for S/F Chinook start tank building |  |  | 956525
Support building: includes start tank store room, bio lab, incubation
rooms,crew restrooms, crew room, water treatment room, larger
food storage area, start tank feed storage room, garage and
and shop spaces. Total foot print area of 18,500sf
84 | Footings, 12" |  |  | 140 | ls | 300 | 42000
85 | Slab, 6" |  |  | 370 | ls | 350 | 129500
86 | High interior walls, 9" |  |  | 340 | cy | 400 | 136000
87 | Low interior walls and exterior walls, 9" |  |  | 340 | cy | 400 | 136000
88 | Ceiling/2nd floor beam/truss system |  |  | 7000 | sf | 15 | 105000
89 | Roof System |  |  | 21000 | sf | 10 | 210000
90 | Mechanical, air handling/plumbing/hydro tank |  |  | 1 | ls | 20000 | 20000
91 | Mechanical, fire sprinklers and pump, specials |  |  | 1 | ls | 100000 | 100000
92 | Shop work bench, welding vent., other specials |  |  | 1 | ls | 30000 | 30000
93 | Pressure filter system |  |  | 1 | ls | 90000 | 90000
94 | 200 ton water chilling (for incubation water) |  |  | 1 | ls | 100000 | 100000
95 | Building heat system |  |  | 1 | ls | 100000 | 100000
96 | Diesel fuel storage |  |  | 1 | ls | 30000 | 30000
97 | UV System |  |  | 1 | ls | 60000 | 60000
98 | Incubation, full heath stacks, w/head trough and piping |  |  | 36 | ea | 4000 | 144000
99 | Electrical, MCCs and other load center panels |  |  | 1 | ls | 500000 | 500000
100 | Power and lighting, general building |  |  | 1 | ls | 50000 | 50000
101 | Roll-up doors 14'x14' |  |  | 4 | ea | 3200 | 12800
102 | Loading dock, adjustable, bumpers |  |  | 1 | ea | 8000 | 8000
|  |  |  | Total for support building |  |  | 2003300
Aeration/settling structure
103 | Slabs, 6" |  |  | 130 | cy | 350 | 45500
104 | Walls, 9" |  |  | 95 | cy | 400 | 38000
105 | Ramp, 8" |  |  | 16 | cy | 350 | 5600
106 | Access gates, double |  |  | 2 | ea | 1000 | 2000
107 | Aerator and electrical controls |  |  | 2 | ea | 5000 | 10000
|  |  |  | Total for aeration/settling structure |  |  | 101100
Detention Pond
108 | Excavation, 11cy scraper, haul 5000 ft |  |  | 10370 | cy | 4 | 41480
109 | Dozer spread, no compaction |  |  | 10370 | cy | 2 | 20740
110 | Liner, 60 mil HDPE |  |  | 5150 | sy | 12 | 61800
111 | Fill over liner, 1ft deep, suitable for wet-land plantings, dozer |  |  | 46.35 | msf | 800 | 37080
112 | Outlet control structure |  |  | 1 | ls | 3000 | 3000
113 | Overflow piping, 18" HDPE |  |  | 250 | lf | 90 | 22500
114 | Fencing, rustic, 3 rail cedar, blend into wetland plantings |  |  | 1000 | lf | 15 | 15000
115 | Wetland style plantings |  |  | 1 | ls | 10000 | 10000
|  |  |  | Total for detention pond |  |  | 211600
Hatchery office and small visitor display building
116 | Structure, single level |  |  | 2000 | sf | 100 | 200000
|  |  |  | Total for Office/Visitor area |  |  | 200000
Site work
117 | Field testing, allowance |  |  | 1 | ls | 100000 | 100000
118 | Temporary power, sani cans, water delivery |  |  | 1 | ls | 50000 | 50000
119 | Temporary site fencing, silt fence and dust control |  |  | 1 | ls | 20000 | 20000
120 | Topsoil stripping, 300hp dozer |  |  | 3500 | cy | 0.65 | 2275
121 | Grading, for pavement and gravel areas |  |  | 18000 | sy | 1 | 18000
122 | Excavation, all facilities except fishway, ladder and attraction water ps |  |  | 1 | ls | 100000 | 100000
123 | Backfill and compaction, various |  |  | 1 | ls | 100000 | 100000
124 | Retaining wall along Half-Sun Road, est 500lf |  |  | 1 | ls | 50000 | 50000
125 | Pavement, 6" base & 4" top |  |  | 10000 | sy | 13 | 130000
126 | Storm drainage system |  |  | 1 | ls | 20000 | 20000
127 | Site lighting |  |  | 1 | ls | 30000 | 30000
128 | Fencing, security, 6ft, 9ga aluminized steel |  |  | 3500 | lf | 30 | 105000
129 | Gates, double swing, 20' open |  |  | 4 | ea | 2000 | 8000
Site piping, various as shown
130 | 8" smolt transfer pipe, portable, Start tanks to Raceways |  |  | 500 | lf | 35 | 17500
131 | 8" smolt transfer pipe, buried, Raceways to smolt transfer area |  |  | 600 | lf | 45 | 27000
132 | 36" start tank room drain to raceway drain |  |  | 300 | lf | 155 | 46500
133 | 48" raceway drain to detention pond |  |  | 750 | lf | 180 | 135000
134 | 30" detention pond drain/overflow |  |  | 250 | lf | 135 | 33750
135 | 48" detention pond drain toward fish ladder |  |  | 1290 | lf | 180 | 232200
136 | 36" continuation to adult holding area |  |  | 470 | lf | 155 | 72850
137 | 30" within adult holding/spawning area |  |  | 450 | lf | 135 | 60750
138 | 30" butterfly valves on piping into adult holding facilities |  |  | 6 | ea | 8000 | 48000
139 | 8" raceway vacuum cleaning drains to aeration/settling facility |  |  | 900 | lf | 55 | 49500
140 | 12" aeration/settling facility drain |  |  | 180 | lf | 70 | 12600
141 | 8" butterfly valve on raceway cleaning drain |  |  | 2 | ea | 700 | 1400
142 | 12" butterfly valve on aeration drain |  |  | 2 | ea | 1200 | 2400
143 | Main site power w/ stand-by generator |  |  | 1 | ls | 100000 | 100000
144 | Site communications for instrumentation/alarms |  |  | 1 | ls | 50000 | 50000
145 | Sewage process system, 10,000 gpd |  |  | 1 | ls | 150000 | 150000
146 | Landscaping |  |  | 1 | ls | 20000 | 20000
147 | Trail relocate |  |  | 1 | ls | 15000 | 15000
|  |  |  | Total for site items |  |  | 1807725
CJD Hatchery Housing Complex - 3 residences and 3 trailer shelters w/utils
148 | Clear and Grub |  |  | 1 | ac | 4000 | 4000
149 | Soil Excavation - Excavate, Haul, Dispose |  |  | 100 | cy | 18 | 1800
150 | Select Fill - Load, Haul, Spread, Compact |  |  | 100 | cy | 61 | 6100
151 | Grading - Fine |  |  | 500 | sy | 4 | 2000
152 | Roadway Improvements - Gravel Road |  |  | 450 | sy | 20 | 9000
153 | Driveways - Gravel |  |  | 500 | sy | 20 | 10000
154 | 2000 Square Foot House with 2- car Garage |  |  | 3 | ea | 100000 | 300000
155 | Sheltered trailer site with utility hookups |  |  | 3 | ea | 10000 | 30000
156 | Well - 6 inch diameter, 400 feet deep |  |  | 1 | ea | 12000 | 12000
157 | Well Pump - 5 HP |  |  | 1 | ea | 2500 | 2500
158 | Group B Water System Approval |  |  | 1 | ea | 5000 | 5000
159 | Pipe - Water supply to residences, 1 inch PVC |  |  | 1000 | lf | 12 | 12000
160 | On site Septic System - 3 Bedroom house |  |  | 3 | ea | 5000 | 15000
161 | On site Septic System - Serves 3 - 3 person trailer sites |  |  | 1 | ea | 5000 | 5000
162 | On site Septic System Design and Approval |  |  | 4 | ea | 2000 | 8000
163 | Telephone |  |  | 1 | ea | 1700 | 1700
164 | Power |  |  | 1 | ls | 10000 | 10000
|  |  |  | Total for Hatchery Housing Complex items |  |  | 434100
165 | Subtotal Raw Costs Hatchery Site with 15% O& 15% P | [5 empty] | 9236267
166 | Mobilization/demobilization | [5 empty] | 270000
167 | Sales Tax @ 9% | [5 empty] | 831264.03
168 | Contingency @ 30% | [5 empty] | 2770880.1
| Total Estimated Cost for Summer/Fall Chinook Programs At CJDH site without COE supplied rearing water | [5 empty] | 13108411.13
169 | Well and reservoir water will be supplied to the hatchery site per COE. Cost shown is for Relief Tunnel Revisions, Intake
Diversion Revisions, Pipeline(s) from dam to hatchery and includes contractor mark-ups for Mob & Demob, site and home office
| bonds and insurance, B&O tax, and State sales tax. | [5 empty] | 3111950
| Total Estimated Cost for Summer/Fall Chinook Programs At CJDH site with COE supplied rearing water | [5 empty] | 16220361.13
Acclimation ponds for Summer/Fall Programs
Riverside Pond - New 53,000 cubic feet acclimation pond
170 | Clear and Grub |  |  | 1 | ac | 4000 | 4000
171 | Dewater |  |  | 1 | ls | 3000 | 3000
172 | Erosion Control - Silt Fence |  |  | 250 | lf | 1 | 250
173 | Soil Excavation - Excavate, Haul, Dispose |  |  | 1500 | cy | 18 | 27000
174 | Rock Excavation - Excavate, Haul, Dispose |  |  | 150 | cy | 27 | 4050
175 | Select Fill - Load, Haul, Spread, Compact |  |  | 300 | cy | 61 | 18300
176 | Grading - Fine |  |  | 1500 | sy | 4 | 6000
177 | Roadway Improvements - Gravel Road |  |  | 2000 | sy | 20 | 40000
178 | Rail Road Crossing |  |  | 1 | ls | 3000 | 3000
179 | Pond Liner - 60 mil HDPE |  |  | 1800 | sy | 10 | 18000
180 | Pond Liner - Attachment to Concrete |  |  | 100 | lf | 50 | 5000
181 | Fencing - Chain Link |  |  | 1200 | lf | 15 | 18000
182 | Fencing - Gate |  |  | 2 | ea | 1100 | 2200
183 | Fencing - Overhead Netting with supports |  |  | 25000 | sf | 4 | 100000
184 | Pipe - Outflow, 18" HDPE |  |  | 300 | lf | 50 | 15000
185 | Pipe Fittings - Outflow, 18" HDPE |  |  | 4 | ea | 450 | 1800
186 | Pipe - Supply, 18" PVC |  |  | 200 | lf | 60 | 12000
187 | Pipe Fittings - Supply, 18" PVC |  |  | 4 | ea | 650 | 2600
188 | Pipe - Supply Header, 12" SCH 10 SST |  |  | 1 | ea | 1600 | 1600
189 | Valves - Supply, 12" Butterfly |  |  | 1 | ea | 1250 | 1250
190 | Outfall - In River with Erosion Protection |  |  | 1 | ea | 2500 | 2500
191 | Outlet Structure - Concrete |  |  | 25 | cy | 600 | 15000
192 | Outlet Structure - Screens, 5 FT Wide |  |  | 2 | ea | 1150 | 2300
193 | Outlet Structure - Stop Logs, 5 FT Wide |  |  | 2 | ea | 1150 | 2300
194 | Outlet Structure - Slide Gate Valve |  |  | 1 | ea | 3550 | 3550
195 | Supply Pump Station - Concrete |  |  | 25 | cy | 600 | 15000
196 | Supply Pump Station - Dual pumps, pipes, valves |  |  | 1 | ea | 21000 | 21000
197 | Supply Pump Station - River inlet and screen |  |  | 1 | ea | 3700 | 3700
198 | Power |  |  | 1 | ls | 12500 | 12500
199 | Controls, Instrumentation, Telemetry |  |  | 1 | ls | 4500 | 4500
|  |  |  | Total for Riverside Pond items |  |  | 365400
Omak Pond - New 53,000 cubic feet acclimation pond
200 | Clear and Grub |  |  | 1 | ac | 4000 | 4000
201 | Dewater |  |  | 1 | ls | 3000 | 3000
202 | Erosion Control - Silt Fence |  |  | 250 | lf | 1 | 250
203 | Demolition - Buildings, Conc, Asphalt |  |  | 1 | ls | 3000 | 3000
204 | Soil Excavation - Excavate, Haul, Dispose |  |  | 1700 | cy | 18 | 30600
205 | Rock Excavation - Excavate, Haul, Dispose |  |  | 200 | cy | 27 | 5400
206 | Select Fill - Load, Haul, Spread, Compact |  |  | 375 | cy | 61 | 22875
207 | Grading - Fine |  |  | 1500 | sy | 4 | 6000
208 | Roadway Improvements - Gravel Road |  |  | 600 | sy | 20 | 12000
209 | Utility Relocations |  |  | 1 | ea | 1000 | 1000
210 | Pond Liner - 60 mil HDPE |  |  | 2200 | sy | 10 | 22000
211 | Pond Liner - Attachment to Concrete |  |  | 100 | lf | 50 | 5000
212 | Fencing - Chain Link |  |  | 1200 | lf | 15 | 18000
213 | Fencing - Gate |  |  | 2 | ea | 1100 | 2200
214 | Fencing - Overhead Netting with supports |  |  | 25000 | sf | 4 | 100000
215 | Pipe - Outflow, 24" HDPE |  |  | 300 | lf | 60 | 18000
216 | Pipe Fittings - Outflow, 24" HDPE |  |  | 4 | ea | 550 | 2200
217 | Pipe - Supply, 18" PVC |  |  | 200 | lf | 60 | 12000
218 | Pipe Fittings - Supply, 18" PVC |  |  | 4 | ea | 550 | 2200
219 | Pipe - Supply Header, 18" SCH 10 SST |  |  | 1 | ea | 2000 | 2000
220 | Valves - Supply, 18" Butterfly |  |  | 1 | ea | 1550 | 1550
221 | Outfall - In River with Erosion Protection |  |  | 1 | ea | 2500 | 2500
222 | Outlet Structure - Concrete |  |  | 25 | cy | 600 | 15000
223 | Outlet Structure - Screens, 5 FT Wide |  |  | 2 | ea | 1150 | 2300
224 | Outlet Structure - Stop Logs, 5 FT Wide |  |  | 2 | ea | 1150 | 2300
225 | Outlet Structure - Slide Gate Valve |  |  | 1 | ea | 3550 | 3550
226 | Supply Pump Station - Concrete |  |  | 25 | cy | 600 | 15000
227 | Supply Pump Station - Dual pumps, pipes, valves |  |  | 1 | ea | 21000 | 21000
228 | Supply Pump Station - River inlet and screen |  |  | 1 | ea | 3700 | 3700
229 | Power |  |  | 1 | ls | 6000 | 6000
230 | Controls, Instrumentation, Telemetry |  |  | 1 | ls | 4500 | 4500
|  |  |  | Total for Omak Pond items |  |  | 349125
Bonaparte Pond - Modify an existing 65,300 cubic feet acclimation pond
231 | Soil Excavation - Excavate, Haul, Dispose |  |  | 100 | cy | 18 | 1800
232 | Select Fill - Load, Haul, Spread, Compact |  |  | 50 | cy | 61 | 3050
233 | Grading - Fine |  |  | 100 | sy | 4 | 400
234 | Pond Liner - 60 mil HDPE |  |  | 100 | sy | 10 | 1000
235 | Pond Liner - Attachment to Concrete |  |  | 100 | lf | 50 | 5000
236 | Pipe - Outflow, 24" HDPE |  |  | 300 | lf | 60 | 18000
237 | Pipe Fittings - Outflow, 24" HDPE |  |  | 4 | ea | 550 | 2200
238 | Outlet Structure - Concrete |  |  | 25 | cy | 600 | 15000
239 | Outlet Structure - Screens, 5 FT Wide |  |  | 2 | ea | 1150 | 2300
240 | Outlet Structure - Stop Logs, 5 FT Wide |  |  | 2 | ea | 1150 | 2300
241 | Outlet Structure - Slide Gate Valve |  |  | 1 | ea | 3550 | 3550
242 | Instrumentation & Telemetry - Water level alarm |  |  | 1 | ls | 2700 | 2700
|  |  |  | Total for Bonaparte Pond items |  |  | 57300
243 | Subtotal Acclimation ponds with 15% O& 15% P | [5 empty] | 771825
244 | Mobilization/demobilization | [5 empty] | 77182.5
245 | Sales Tax @ 9% | [5 empty] | 69464.25
246 | Contingency @ 30% | [5 empty] | 231547.5
| Total, summer/fall Chinook acclimation ponds | [5 empty] | 1150019.25
|  | TOTAL for Summer/Fall Chinook Programs with COE supplied water systems |  |  |  |  | 17370380.38
Additional Cost for Spring programs at CJDH site
ITEM | DESCRIPTION |  |  | QTY | UNIT | UNIT PRICE | COST
Develop well water supply from park 2.5 miles upstream. See note 3 below
247 | Wells to supply 2.5cfs ea. |  |  | 10 | ls | 70000 | 700000
248 | 30" collection and main piping to hatchery |  |  | 13200 | lf | 135 | 1782000
|  |  |  | Total for additional wells |  |  | 2482000
Piping from S/F raceways to Spring raceways
249 | 30" diam, HDPE |  |  | 400 | lf | 135 | 54000
250 | 24" diam, HDPE |  |  | 400 | lf | 115 | 46000
251 | 48" diam, HDPE |  |  | 20 | lf | 180 | 3600
252 | 30" various fittings |  |  | 1 | ls | 15000 | 15000
253 | 24" various fittings |  |  | 1 | ls | 10000 | 10000
254 | 48" various fittings |  |  | 1 | ls | 5000 | 5000
255 | 30" flow meter |  |  | 1 | ea | 3000 | 3000
256 | 24" flow meter |  |  | 1 | ea | 2500 | 2500
257 | 24"x24" sluice gate at raceways |  |  | 2 | ea | 10000 | 20000
258 | 30"x30" sluice gate at raceways |  |  | 2 | ea | 12000 | 24000
|  |  |  | Total to raceways |  |  | 183100
Spring Chinook Raceways ( bank of 28 units)
259 | Concrete slabs, 6" |  |  | 323 | cy | 350 | 113050
260 | Concrete walls, 9" |  |  | 521 | cy | 400 | 208400
261 | Sluice gates, 36"x18", inlet, topping |  |  | 28 | ea | 3000 | 84000
262 | Stop logs, 3"x 6'x4' |  |  | 2420 | bf | 3 | 7260
263 | Flow distribution plate, SS, 1/4" |  |  | 1064 | sf | 10 | 10640
264 | Screens, SS, 4 per raceway, var sizes, 50% redun. |  |  | 9072 | sf | 10 | 90720
265 | Grating, fiberglass, supply & drain channels |  |  | 2688 | sf | 7 | 18816
266 | Grating, fiberglass, center walls |  |  | 2828 | sf | 10 | 28280
267 | Feeders, demand, 2 per raceway |  |  | 56 | ea | 1200 | 67200
268 | Misc. metals, braces, hangers, channels |  |  | 1 | ls | 23000 | 23000
269 | 6" raceway vacuum cleaning drains to aeration/settling facility |  |  | 300 | lf | 45 | 13500
|  |  |  | Total for Spring Chinook raceway bank |  |  | 664866
Start tank building & incubation area for Spring Chinook
270 | Footings |  |  | 20 | ls | 300 | 6000
271 | Slabs |  |  | 204 | ls | 350 | 71400
272 | Exterior walls |  |  | 61 | ls | 400 | 24400
273 | Ceiling/2nd floor beam/truss system |  |  | 6000 | sf | 15 | 90000
274 | Roof system |  |  | 6360 | sf | 10 | 63600
275 | Piping, extend two water supply systems |  |  | 2 | systems | 37000 | 74000
276 | Piping, drain and fish transfer to raceways |  |  | 1 | ls | 10000 | 10000
277 | Lighting and power |  |  | 1 | ls | 5000 | 5000
278 | Increase of chiller size to handle increased incubator flow |  |  | 1 | ls | 40000 | 40000
279 | Heath Incubators |  |  | 16 | stacks | 4000 | 64000
280 | Start tanks, alum. 4X40X3deep |  |  | 20 | ea | 4000 | 80000
281 | 6" Start tank vacuum cleaning pipe to S/F raceways |  |  | 110 | ls | 45 | 4950
|  |  |  | Total for Spring Chinook start tank building |  |  | 533350
282 | Subtotal Raw Costs with 15% O& 15% P | [5 empty] | 3863316
283 | Mobilization/demobilization | [5 empty] | 30000
284 | Sales Tax @ 9% | [5 empty] | 347698.44
285 | Contingency @ 30% | [5 empty] | 1158994.8
| Additional Cost at CJDH for Spring Chinook Programs | [5 empty] | 5400009.24
Acclimation ponds for Spring Programs
Saint Mary's Mission Pond - Modify an existing acclimation pond
286 | Dewater |  |  | 1 | ls | 3000 | 3000
287 | Demolition - Remove pond grating and supports |  |  | 1 | ls | 1000 | 1000
288 | Grading - Fine |  |  | 100 | sy | 4 | 400
289 | Fencing - Chain Link |  |  | 300 | lf | 15 | 4500
290 | Fencing - Gate |  |  | 2 | ea | 1100 | 2200
291 | Fencing - Overhead Netting with supports |  |  | 4000 | sf | 4 | 16000
292 | Channels - Concrete |  |  | 25 | cy | 600 | 15000
293 | Channel - Tail and Head Screens |  |  | 2 | ea | 1150 | 2300
294 | River Intake - Concrete Wing Wall |  |  | 10 | cy | 600 | 6000
295 | Power - Backup system for Well |  |  | 1 | ls | 3700 | 3700
296 | Instrumentation & Telemetry - Water level alarm |  |  | 1 | ls | 2700 | 2700
|  |  |  | Total for St. Mary's Mission Pond items |  |  | 56800
Ellisforde Pond - Modifications to an existing 121,500 cubic feet acclimation pond
297 | Soil Excavation - Excavate, Haul, Dispose |  |  | 100 | cy | 18 | 1800
298 | Select Fill - Load, Haul, Spread, Compact |  |  | 50 | cy | 61 | 3050
299 | Grading - Fine |  |  | 100 | sy | 4 | 400
300 | Pond Liner - 60 mil HDPE |  |  | 100 | sy | 10 | 1000
301 | Pond Liner - Attachment to Concrete |  |  | 100 | lf | 50 | 5000
302 | Pipe - Outflow, 24" HDPE |  |  | 300 | lf | 60 | 18000
303 | Pipe Fittings - Outflow, 24" HDPE |  |  | 4 | ea | 550 | 2200
304 | Outlet Structure - Concrete |  |  | 25 | cy | 600 | 15000
305 | Outlet Structure - Screens, 5 FT Wide |  |  | 2 | ea | 1150 | 2300
306 | Outlet Structure - Stop Logs, 5 FT Wide |  |  | 2 | ea | 1150 | 2300
307 | Outlet Structure - Slide Gate Valve |  |  | 1 | ea | 3550 | 3550
308 | Instrumentation & Telemetry - Water level alarm |  |  | 1 | ls | 2700 | 2700
|  |  |  | Total for Ellisforde Pond items |  |  | 57300
| Total, spring chinook acclimation ponds | [5 empty] | 114100
309 | Subtotal Spring Acclimation Pond Costs with 15% O& 15% P | [5 empty] | 114100
310 | Mobilization/demobilization | [5 empty] | 11410
311 | Sales Tax @ 9% | [5 empty] | 10269
312 | Contingency @ 30% | [5 empty] | 34230
| Additional Cost for Ponds for Spring Chinook Programs | [5 empty] | 170009
|  |  | TOTAL for all facilities for the Spring Chinook Programs |  |  |  | 5570018.24
Summary
313 | Total Estimated Cost for Summer/Fall Chinook Programs at CJDH with COE supplied rearing water | [5 empty] | 16220361.13
314 | Total, summer/fall chinook acclimation ponds | [5 empty] | 1150019.25
|  | TOTAL for all Summer/fall chinook programs |  |  |  |  | 17370380.38
315 | Additional Cost at CJDH for Spring Chinook Programs | [5 empty] | 5400009.24
316 | Additional Cost for Spring Chinook acclimation ponds | [5 empty] | 170009
|  | TOTAL for all Spring chinook program facilities |  |  |  |  | 5570018.24
|  | TOTAL for All Chinook Programs with COE supplied water systems |  |  |  |  | 22940398.62
NOTES:
1. Site piping cost portion attributed to increased pipe sizes due to Spring Chinook program is about $150,000.
2. An item not included in the above cost estimate is an Electric fish directing fence.
3. Well water supply concept based upon information from COE about availability of water in upstream park.

## Table_3,4,5,16,22_Constsum
Capital Construction Costs for Summer/ Fall Chinook Program
| DESCRIPTION OF AREA | [5 empty] | ESTIMATED COST
WATER SUPPLY
COE water systems for hatchery rearing shown in line item 169
Piping based upon COE termination at 10 feet from headbox.
1 | 30" diam, HDPE, Tunnel water to headbox |  |  | 40 | lf | 135 | 5400
2 | 36" diam, HDPE, Reservoir water to headbox |  |  | 40 | lf | 155 | 6200
3 | 36"Butterfly valve on reservoir water at headbox w/electrical controls |  |  | 1 | ea | 10000 | 10000
4 | 36" diam, HDPE overflow to 48" drain |  |  | 250 | lf | 155 | 38750
|  |  |  | Total to headbox |  |  | 60350
Headbox with drum filter on Reservoir supply
5 | Concrete footings, 12" |  |  | 40 | cy | 300 | 12000
6 | Concrete slab on grade, 6" |  |  | 8 | cy | 300 | 2400
7 | Concrete slab, 2nd level, 8" |  |  | 24 | cy | 400 | 9600
8 | Concrete exterior walls, 9" |  |  | 240 | cy | 500 | 120000
9 | Concrete weir walls, 9" |  |  | 30 | cy | 400 | 12000
10 | Grating, fiberglass |  |  | 304 | sf | 7 | 2128
11 | Drum Filter system |  |  | 1 | ls | 500000 | 500000
12 | Stairs, galv steel, 4' wide, 50 risers |  |  | 50 | risers | 225 | 11250
13 | Landings, 4x4 |  |  | 2 | ea | 600 | 1200
14 | Doors, metal, 36x78, with hardware |  |  | 2 | ea | 350 | 700
15 | Roof, Metal |  |  | 650 | sf | 10 | 6500
16 | Louvers, SS, 36x36 |  |  | 2 | ea | 400 | 800
|  |  |  | Total for headbox |  |  | 678578
Piping from headbox to S/F raceways
17 | 36" diam, HDPE, Reservoir water |  |  | 660 | lf | 155 | 102300
18 | 30" diam, HDPE, Well water |  |  | 660 | lf | 135 | 89100
19 | 36" various fittings |  |  | 1 | ls | 25000 | 25000
20 | 30" various fittings |  |  | 1 | ls | 20000 | 20000
21 | 24" flow meter |  |  | 2 | ea | 2500 | 5000
22 | 30" flow meter |  |  | 2 | ea | 3000 | 6000
23 | 24"x24" sluice gate at raceways |  |  | 4 | ea | 10000 | 40000
24 | 30"x30" sluice gate at raceways |  |  | 4 | ea | 12000 | 48000
|  |  |  | Total to raceways |  |  | 335400
500cfs Pumped Fish Ladder Attraction Water
Vert turb pumps within screened 50wx40dx30h
structure beside entrance to fish ladder
25 | Concrete slabs, 12" |  |  | 120 | cy | 350 | 42000
26 | Concrete walls, 12" |  |  | 288 | cy | 500 | 144000
27 | (100cfs)45,000gpm/10'TDH, 150hp, 430rpm pump |  |  | 5 | ea | 25000 | 125000
Hydro-foil pump 48PL
28 | Inlet screen structure (1" ss rods @ 1.5" c-c) |  |  | 18200 | lb | 10 | 182000
29 | Sheet pile around excavation, drive & extract |  |  | 13000 | sf | 12 | 156000
30 | Excavation, 1cy clam shell, haul 1/2 mi |  |  | 4000 | cy | 10 | 40000
31 | Backfill and use for access road fill |  |  | 4000 | cy | 10 | 40000
32 | Rock armor replacement |  |  | 1 | ls | 20000 | 20000
33 | Access road to structure |  |  | 1 | ls | 10000 | 10000
34 | Electrical Panels and misc |  |  | 1 | ls | 20000 | 20000
35 | Gratings, fiberglass |  |  | 1700 | sf | 7 | 11900
36 | Structural steel |  |  | 8000 | lb | 10 | 80000
|  |  |  | Total for attraction water |  |  | 870900
RACEWAYS
Early S/F Chinook Raceways ( bank of 20 units)
37 | Concrete slabs, 6" |  |  | 384 | cy | 350 | 134400
38 | Concrete walls, 9" |  |  | 414 | cy | 400 | 165600
39 | Sluice gates, 36"x18", inlet, topping |  |  | 20 | ea | 3000 | 60000
40 | Stop logs, 3"x 6'x4' |  |  | 1440 | bf | 3 | 4320
41 | Flow distribution plate, SS, 1/4" |  |  | 633 | sf | 10 | 6330
42 | Screens, SS, 4 per raceway, var sizes, 50% redun. |  |  | 5400 | sf | 10 | 54000
43 | Grating, fiberglass, supply & drain channels |  |  | 1600 | sf | 7 | 11200
44 | Grating, fiberglass, center walls |  |  | 1680 | sf | 10 | 16800
45 | Feeders, demand, 2 per raceway |  |  | 40 | ea | 1200 | 48000
46 | Misc. metals, braces, hangers, channels |  |  | 1 | ls | 17000 | 17000
47 | 6" Raceway vacuum cleaning drain to connection w/ 6" from Late S/F |  |  | 375 | lf | 45 | 16875
|  |  |  | Total for Early S/F raceway bank |  |  | 534525
Late S/F Chinook Raceways ( bank of 24 units)
48 | Concrete slabs, 6" |  |  | 461 | cy | 350 | 161350
49 | Concrete walls, 9" |  |  | 496 | cy | 400 | 198400
50 | Sluice gates, 36"x18", inlet, topping |  |  | 24 | ea | 3000 | 72000
51 | Stop logs, 3"x 6'x4' |  |  | 1728 | bf | 3 | 5184
52 | Flow distribution plate, SS, 1/4" |  |  | 760 | sf | 10 | 7600
53 | Screens, SS, 4 per raceway, var sizes, 50% redun. |  |  | 6480 | sf | 10 | 64800
54 | Grating, fiberglass, supply & drain channels |  |  | 1920 | sf | 7 | 13440
55 | Grating, fiberglass, center walls |  |  | 2020 | sf | 10 | 20200
56 | Feeders, demand, 2 per raceway |  |  | 48 | ea | 1200 | 57600
57 | Misc. metals, braces, hangers, channels |  |  | 1 | ls | 17000 | 17000
58 | 6" Raceway vacuum cleaning drain to aeration/settling facility |  |  | 480 | lf | 45 | 21600
|  |  |  | Total for Late S/F raceway bank |  |  | 639174
BROOD HOLDING AND EGGTAKES
Spawn House
59 | Building Area, Concrete lower walls w/ upper metal, roof at 6:12 slope |  |  | 1224 | sf | 60 | 73440
60 | Pumps for sorting tubes water supply |  |  | 1 | ea | 1000 | 1000
61 | Valves for fish sorting tubes |  |  | 1 | ls | 2000 | 2000
62 | Mechanical, plumbing/air compressor |  |  | 1 | ls | 2000 | 2000
63 | Electrical- pump controls/lighting/power |  |  | 1 | ls | 4000 | 4000
64 | Misc. equipment for anesthetic treatment |  |  | 1 | ls | 4000 | 4000
|  |  |  | Total for spawn house |  |  | 86440
Fish ladder and holding/sorting tanks
| Excavation w/1.5 cy hoe and haul 1 mile |  |  | 500 | cy | 8 | 4000
| Slab on grade and footings |  |  | 134 | cy | 300 | 40200
| Exterior walls, 9" |  |  | 460 | cy | 400 | 184000
| Weir walls, 9" |  |  | 33 | cy | 500 | 16500
| Backfill and compaction |  |  | 2150 | cy | 15 | 32250
| Grating cover |  |  | 1800 | sf | 10 | 18000
| Vehicle fish ladder crossing cover |  |  | 36 | ea | 600 | 21600
|  |  |  | Total for ladder and holding/sorting |  |  | 316550
REARING BUILDING
Start tank building for S/F Chinook
| Footings, 12" |  |  | 50 | ls | 300 | 15000
| Slabs, 9" |  |  | 360 | ls | 350 | 126000
| Exterior walls, 9" |  |  | 200 | ls | 400 | 80000
| Ceiling/2nd floor beam/truss system |  |  | 12000 | sf | 15 | 180000
| Stairs, metal, 25 risers |  |  | 25 | risers | 225 | 5625
| Roof system |  |  | 12640 | sf | 10 | 126400
| Piping, four systems for supply, throughout building |  |  | 2 | systems | 75000 | 150000
| Piping, drain and fish transfer to raceways |  |  | 1 | ls | 20000 | 20000
| Lighting and power |  |  | 1 | ls | 20000 | 20000
| Start tanks, alum. 4X40X3deep |  |  | 40 | ea | 4000 | 160000
| 6" start tank vacuum drain to 6" line from Early S/F raceways |  |  | 600 | lf | 45 | 27000
| 36" drain pipe, HDPE, to Early S/F 48" raceway drain |  |  | 300 | lf | 155 | 46500
|  |  |  | Total for S/F Chinook start tank building |  |  | 956525
SUPPORT BUILDING
Support building: includes start tank store room, bio lab, incubation rooms,crew restrooms, crew room, water treatment room, larger food storage area, start tank feed storage room, garage and shop spaces. Total foot print area of 18,500sf
| Footings, 12" |  |  | 140 | ls | 300 | 42000
| Slab, 6" |  |  | 370 | ls | 350 | 129500
| High interior walls, 9" |  |  | 340 | cy | 400 | 136000
| Low interior walls and exterior walls, 9" |  |  | 340 | cy | 400 | 136000
| Ceiling/2nd floor beam/truss system |  |  | 7000 | sf | 15 | 105000
| Roof System |  |  | 21000 | sf | 10 | 210000
| Mechanical, air handling/plumbing/hydro tank |  |  | 1 | ls | 20000 | 20000
| Mechanical, fire sprinklers and pump, specials |  |  | 1 | ls | 100000 | 100000
| Shop work bench, welding vent., other specials |  |  | 1 | ls | 30000 | 30000
| Pressure filter system |  |  | 1 | ls | 90000 | 90000
| 200 ton water chilling (for incubation water) |  |  | 1 | ls | 100000 | 100000
| Building heat system |  |  | 1 | ls | 100000 | 100000
| Diesel fuel storage |  |  | 1 | ls | 30000 | 30000
| UV System |  |  | 1 | ls | 60000 | 60000
| Incubation, full heath stacks, w/head trough and piping |  |  | 36 | ea | 4000 | 144000
| Electrical, MCCs and other load center panels |  |  | 1 | ls | 500000 | 500000
| Power and lighting, general building |  |  | 1 | ls | 50000 | 50000
| Roll-up doors 14'x14' |  |  | 4 | ea | 3200 | 12800
| Loading dock, adjustable, bumpers |  |  | 1 | ea | 8000 | 8000
|  |  |  | Total for support building |  |  | 2003300
WATER TREATMENT INFLUENT AND EFFLUENT
Aeration/settling structure
| Slabs, 6" |  |  | 130 | cy | 350 | 45500
| Walls, 9" |  |  | 95 | cy | 400 | 38000
| Ramp, 8" |  |  | 16 | cy | 350 | 5600
| Access gates, double |  |  | 2 | ea | 1000 | 2000
| Aerator and electrical controls |  |  | 2 | ea | 5000 | 10000
|  |  |  | Total for aeration/settling structure |  |  | 101100
Detention Pond
| Excavation, 11cy scraper, haul 5000 ft |  |  | 10370 | cy | 4 | 41480
| Dozer spread, no compaction |  |  | 10370 | cy | 2 | 20740
| Liner, 60 mil HDPE |  |  | 5150 | sy | 12 | 61800
| Fill over liner, 1ft deep, suitable for wet-land plantings, dozer |  |  | 46.35 | msf | 800 | 37080
| Outlet control structure |  |  | 1 | ls | 3000 | 3000
| Overflow piping, 18" HDPE |  |  | 250 | lf | 90 | 22500
| Fencing, rustic, 3 rail ceder, blend into wetland plantings |  |  | 1000 | lf | 15 | 15000
| Wetland style plantings |  |  | 1 | ls | 10000 | 10000
|  |  |  | Total for detention pond |  |  | 211600
OFFICE AND OTHER
Hatchery office and small visitor display building
| Structure, single level |  |  | 2000 | sf | 100 | 200000
|  |  |  | Total for Office/Visitor area |  |  | 200000
SITE WORK AND UTILITIES
Site work and Utilities
| Field testing, allowance |  |  | 1 | ls | 100000 | 100000
| Temporary power, sani cans, water delivery |  |  | 1 | ls | 50000 | 50000
| Temporary site fencing, silt fence and dust control |  |  | 1 | ls | 20000 | 20000
| Topsoil stripping, 300hp dozer |  |  | 3500 | cy | 0.65 | 2275
| Grading, for pavement and gravel areas |  |  | 18000 | sy | 1 | 18000
| Excavation, all facilities except fishway, ladder and attraction water ps |  |  | 1 | ls | 100000 | 100000
| Backfill and compaction, various |  |  | 1 | ls | 100000 | 100000
| Retaining wall along Half-Sun Road, est 500lf |  |  | 1 | ls | 50000 | 50000
| Pavement, 6" base & 4" top |  |  | 10000 | sy | 13 | 130000
| Storm drainage system |  |  | 1 | ls | 20000 | 20000
| Site lighting |  |  | 1 | ls | 30000 | 30000
| Fencing, security, 6ft, 9ga aluminized steel |  |  | 3500 | lf | 30 | 105000
| Gates, double swing, 20' open |  |  | 4 | ea | 2000 | 8000
Site piping, various as shown
| 8" smolt transfer pipe, portable, Start tanks to Raceways |  |  | 500 | lf | 35 | 17500
| 8" smolt transfer pipe, buried, Raceways to smolt transfer area |  |  | 600 | lf | 45 | 27000
| 36" start tank room drain to raceway drain |  |  | 300 | lf | 155 | 46500
| 48" raceway drain to detention pond |  |  | 750 | lf | 180 | 135000
| 30" detention pond drain/overflow |  |  | 250 | lf | 135 | 33750
| 48" detention pond drain toward fish ladder |  |  | 1290 | lf | 180 | 232200
| 36" continuation to adult holding area |  |  | 470 | lf | 155 | 72850
| 30" within adult holding/spawning area |  |  | 450 | lf | 135 | 60750
| 30" butterfly valves on piping into adult holding facilities |  |  | 6 | ea | 8000 | 48000
| 8" raceway vacuum cleaning drains to aeration/settling facility |  |  | 900 | lf | 55 | 49500
| 12" aeration/settling facility drain |  |  | 180 | lf | 70 | 12600
| 8" butterfly valve on raceway cleaning drain |  |  | 2 | ea | 700 | 1400
| 12" butterfly valve on aeration drain |  |  | 2 | ea | 1200 | 2400
| Main site power w/ stand-by generator |  |  | 1 | ls | 100000 | 100000
| Site communications for instrumentation/alarms |  |  | 1 | ls | 50000 | 50000
| Sewage process system, 10,000 gpd |  |  | 1 | ls | 150000 | 150000
| Landscaping |  |  | 1 | ls | 20000 | 20000
| Trail relocate |  |  | 1 | ls | 15000 | 15000
|  |  |  | Total for site items |  |  | 1807725
HOUSING
CJD Hatchery Housing Complex - 3 residences and 3 trailer shelters w/utils
| Clear and Grub |  |  | 1 | ac | 4000 | 4000
| Soil Excavation - Excavate, Haul, Dispose |  |  | 100 | cy | 18 | 1800
| Select Fill - Load, Haul, Spread, Compact |  |  | 100 | cy | 61 | 6100
| Grading - Fine |  |  | 500 | sy | 4 | 2000
| Roadway Improvements - Gravel Road |  |  | 450 | sy | 20 | 9000
| Driveways - Gravel |  |  | 500 | sy | 20 | 10000
| 2000 Square Foot House with 2- car Garage |  |  | 3 | ea | 100000 | 300000
| Sheltered trailer site with utility hookups |  |  | 3 | ea | 10000 | 30000
| Well - 6 inch diameter, 400 feet deep |  |  | 1 | ea | 12000 | 12000
| Well Pump - 5 HP |  |  | 1 | ea | 2500 | 2500
| Group B Water System Approval |  |  | 1 | ea | 5000 | 5000
| Pipe - Water supply to residences, 1 inch PVC |  |  | 1000 | lf | 12 | 12000
| On site Septic System - 3 Bedroom house |  |  | 3 | ea | 5000 | 15000
| On site Septic System - Serves 3 - 3 person trailer sites |  |  | 1 | ea | 5000 | 5000
| On site Septic System Design and Approval |  |  | 4 | ea | 2000 | 8000
| Telephone |  |  | 1 | ea | 1700 | 1700
|  |  |  | 1 | ls |  | 10000
|  |  |  | Total for Hatchery Housing Complex items |  | Total for Housing Costs | 434100
MARKUPS AND OTHER DIRECT COSTS
| Subtotal Raw Costs Hatchery Site with 15% O& 15% P | [5 empty] | 9236267
| Mobilization/demobilization | [5 empty] | 270000
| Sales Tax @ 9% | [5 empty] | 831264.03
| Contingency @ 30% | [5 empty] | 2770880.1
| Total Estimated Cost for Summer/Fall Chinook Programs At CJDH site without COE supplied rearing water | [5 empty] | 13108411.13
COE WATER SUPPLY
Well and reservoir water will be supplied to the hatchery site per COE. Cost shown is for Relief Tunnel Revisions, Intake Diversion Revisions, Pipeline(s) from dam to hatchery and includes contractor mark-ups for Mob & Demob, site and home office bonds a
| Total for COE Water Supply | [5 empty] | 3111950
| Total Estimated Cost for Summer/Fall Chinook Programs at CJDH site with COE supplied rearing water | [5 empty] | 16220361.13
Acclimation ponds for Summer/Fall Chinook Program
Riverside Pond - New 53,000 cubic feet acclimation pond
| Clear and Grub |  |  | 1 | ac | 4000 | 4000
| Dewater |  |  | 1 | ls | 3000 | 3000
| Erosion Control - Silt Fence |  |  | 250 | lf | 1 | 250
| Soil Excavation - Excavate, Haul, Dispose |  |  | 1500 | cy | 18 | 27000
| Rock Excavation - Excavate, Haul, Dispose |  |  | 150 | cy | 27 | 4050
| Select Fill - Load, Haul, Spread, Compact |  |  | 300 | cy | 61 | 18300
| Grading - Fine |  |  | 1500 | sy | 4 | 6000
| Roadway Improvements - Gravel Road |  |  | 2000 | sy | 20 | 40000
| Rail Road Crossing |  |  | 1 | ls | 3000 | 3000
| Pond Liner - 60 mil HDPE |  |  | 1800 | sy | 10 | 18000
| Pond Liner - Attachment to Concrete |  |  | 100 | lf | 50 | 5000
| Fencing - Chain Link |  |  | 1200 | lf | 15 | 18000
| Fencing - Gate |  |  | 2 | ea | 1100 | 2200
| Fencing - Overhead Netting with supports |  |  | 25000 | sf | 4 | 100000
| Pipe - Outflow, 18" HDPE |  |  | 300 | lf | 50 | 15000
| Pipe Fittings - Outflow, 18" HDPE |  |  | 4 | ea | 450 | 1800
| Pipe - Supply, 18" PVC |  |  | 200 | lf | 60 | 12000
| Pipe Fittings - Supply, 18" PVC |  |  | 4 | ea | 650 | 2600
| Pipe - Supply Header, 12" SCH 10 SST |  |  | 1 | ea | 1600 | 1600
| Valves - Supply, 12" Butterfly |  |  | 1 | ea | 1250 | 1250
| Outfall - In River with Erosion Protection |  |  | 1 | ea | 2500 | 2500
| Outlet Structure - Concrete |  |  | 25 | cy | 600 | 15000
| Outlet Structure - Screens, 5 FT Wide |  |  | 2 | ea | 1150 | 2300
| Outlet Structure - Stop Logs, 5 FT Wide |  |  | 2 | ea | 1150 | 2300
| Outlet Structure - Slide Gate Valve |  |  | 1 | ea | 3550 | 3550
| Supply Pump Station - Concrete |  |  | 25 | cy | 600 | 15000
| Supply Pump Station - Dual pumps, pipes, valves |  |  | 1 | ea | 21000 | 21000
| Supply Pump Station - River inlet and screen |  |  | 1 | ea | 3700 | 3700
| Power |  |  | 1 | ls | 12500 | 12500
| Controls, Instrumentation, Telemetry |  |  | 1 | ls | 4500 | 4500
|  |  |  | Total for Riverside Pond items |  |  | 365400
Omak Pond - New 53,000 cubic feet acclimation pond
| Clear and Grub |  |  | 1 | ac | 4000 | 4000
| Dewater |  |  | 1 | ls | 3000 | 3000
| Erosion Control - Silt Fence |  |  | 250 | lf | 1 | 250
| Demolition - Buildings, Conc, Asphalt |  |  | 1 | ls | 3000 | 3000
| Soil Excavation - Excavate, Haul, Dispose |  |  | 1700 | cy | 18 | 30600
| Rock Excavation - Excavate, Haul, Dispose |  |  | 200 | cy | 27 | 5400
| Select Fill - Load, Haul, Spread, Compact |  |  | 375 | cy | 61 | 22875
| Grading - Fine |  |  | 1500 | sy | 4 | 6000
| Roadway Improvements - Gravel Road |  |  | 600 | sy | 20 | 12000
| Utility Relocations |  |  | 1 | ea | 1000 | 1000
| Pond Liner - 60 mil HDPE |  |  | 2200 | sy | 10 | 22000
| Pond Liner - Attachment to Concrete |  |  | 100 | lf | 50 | 5000
| Fencing - Chain Link |  |  | 1200 | lf | 15 | 18000
| Fencing - Gate |  |  | 2 | ea | 1100 | 2200
| Fencing - Overhead Netting with supports |  |  | 25000 | sf | 4 | 100000
| Pipe - Outflow, 24" HDPE |  |  | 300 | lf | 60 | 18000
| Pipe Fittings - Outflow, 24" HDPE |  |  | 4 | ea | 550 | 2200
| Pipe - Supply, 18" PVC |  |  | 200 | lf | 60 | 12000
| Pipe Fittings - Supply, 18" PVC |  |  | 4 | ea | 550 | 2200
| Pipe - Supply Header, 18" SCH 10 SST |  |  | 1 | ea | 2000 | 2000
| Valves - Supply, 18" Butterfly |  |  | 1 | ea | 1550 | 1550
| Outfall - In River with Erosion Protection |  |  | 1 | ea | 2500 | 2500
| Outlet Structure - Concrete |  |  | 25 | cy | 600 | 15000
| Outlet Structure - Screens, 5 FT Wide |  |  | 2 | ea | 1150 | 2300
| Outlet Structure - Stop Logs, 5 FT Wide |  |  | 2 | ea | 1150 | 2300
| Outlet Structure - Slide Gate Valve |  |  | 1 | ea | 3550 | 3550
| Supply Pump Station - Concrete |  |  | 25 | cy | 600 | 15000
| Supply Pump Station - Dual pumps, pipes, valves |  |  | 1 | ea | 21000 | 21000
| Supply Pump Station - River inlet and screen |  |  | 1 | ea | 3700 | 3700
| Power |  |  | 1 | ls | 6000 | 6000
| Controls, Instrumentation, Telemetry |  |  | 1 | ls | 4500 | 4500
|  |  |  | Total for Omak Pond items |  |  | 349125
Bonaparte Pond - Modify an existing 65,300 cubic feet acclimation pond
| Soil Excavation - Excavate, Haul, Dispose |  |  | 100 | cy | 18 | 1800
| Select Fill - Load, Haul, Spread, Compact |  |  | 50 | cy | 61 | 3050
| Grading - Fine |  |  | 100 | sy | 4 | 400
| Pond Liner - 60 mil HDPE |  |  | 100 | sy | 10 | 1000
| Pond Liner - Attachment to Concrete |  |  | 100 | lf | 50 | 5000
| Pipe - Outflow, 24" HDPE |  |  | 300 | lf | 60 | 18000
| Pipe Fittings - Outflow, 24" HDPE |  |  | 4 | ea | 550 | 2200
| Outlet Structure - Concrete |  |  | 25 | cy | 600 | 15000
| Outlet Structure - Screens, 5 FT Wide |  |  | 2 | ea | 1150 | 2300
| Outlet Structure - Stop Logs, 5 FT Wide |  |  | 2 | ea | 1150 | 2300
| Outlet Structure - Slide Gate Valve |  |  | 1 | ea | 3550 | 3550
| Instrumentation & Telemetry - Water level alarm |  |  | 1 | ls | 2700 | 2700
|  |  |  | Total for Bonaparte Pond items |  |  | 57300
MARKUPS AND OTHER DIRECT COSTS
| Subtotal Acclimation ponds with 15% O& 15% P | [5 empty] | 771825
| Mobilization/demobilization | [5 empty] | 77182.5
| Sales Tax @ 9% | [5 empty] | 69464.25
| Contingency @ 30% | [5 empty] | 231547.5
| Total, Summer/fall Chinook acclimation ponds | [5 empty] | 1150019.25
|  | Total for Summer/Fall Chinook Programs with COE supplied water systems |  |  |  |  | 17370380.38
CAPITAL CONSTRUCTION COSTS FOR SPRING CHINOOK PROGRAMS
| DESCRIPTION |  |  | QTY | UNIT | ESTIMATED COST
WATER SUPPLY
Develop well water supply from park 2.5 miles upstream
1 | Wells to supply 2.5cfs ea. |  |  | 10 | ls | 70000 | 700000
2 | 30" collection and main piping to hatchery |  |  | 13200 | lf | 135 | 1782000
|  |  |  | Total for additional wells |  |  | 2482000
Piping from S/F raceways to Spring raceways
3 | 30" diam, HDPE |  |  | 400 | lf | 135 | 54000
4 | 24" diam, HDPE |  |  | 400 | lf | 115 | 46000
5 | 48" diam, HDPE |  |  | 20 | lf | 180 | 3600
6 | 30" various fittings |  |  | 1 | ls | 15000 | 15000
7 | 24" various fittings |  |  | 1 | ls | 10000 | 10000
8 | 48" various fittings |  |  | 1 | ls | 5000 | 5000
9 | 30" flow meter |  |  | 1 | ea | 3000 | 3000
10 | 24" flow meter |  |  | 1 | ea | 2500 | 2500
11 | 24"x24" sluice gate at raceways |  |  | 2 | ea | 10000 | 20000
12 | 30"x30" sluice gate at raceways |  |  | 2 | ea | 12000 | 24000
|  |  |  | Total to raceways |  |  | 183100
RACEWAYS
Spring Chinook Raceways ( bank of 28 units)
13 | Concrete slabs, 6" |  |  | 323 | cy | 350 | 113050
14 | Concrete walls, 9" |  |  | 521 | cy | 400 | 208400
15 | Sluice gates, 36"x18", inlet, topping |  |  | 28 | ea | 3000 | 84000
16 | Stop logs, 3"x 6'x4' |  |  | 2420 | bf | 3 | 7260
17 | Flow distribution plate, SS, 1/4" |  |  | 1064 | sf | 10 | 10640
18 | Screens, SS, 4 per raceway, var sizes, 50% redun. |  |  | 9072 | sf | 10 | 90720
19 | Grating, fiberglass, supply & drain channels |  |  | 2688 | sf | 7 | 18816
20 | Grating, fiberglass, center walls |  |  | 2828 | sf | 10 | 28280
21 | Feeders, demand, 2 per raceway |  |  | 56 | ea | 1200 | 67200
22 | Misc. metals, braces, hangers, channels |  |  | 1 | ls | 23000 | 23000
23 | 6" raceway vacuum cleaning drains to aeration/settling facility |  |  | 300 | lf | 45 | 13500
|  |  |  | Total for Spring Chinook raceway bank |  |  | 664866
REARING AND INCUBATION ADDITIONAL BUILDING SPACE
Start tank building & incubation area for Spring Chinook
24 | Footings |  |  | 20 | ls | 300 | 6000
25 | Slabs |  |  | 204 | ls | 350 | 71400
26 | Exterior walls |  |  | 61 | ls | 400 | 24400
27 | Ceiling/2nd floor beam/truss system |  |  | 6000 | sf | 15 | 90000
28 | Roof system |  |  | 6360 | sf | 10 | 63600
29 | Piping, extend two water supply systems |  |  | 2 | systems | 37000 | 74000
30 | Piping, drain and fish transfer to raceways |  |  | 1 | ls | 10000 | 10000
31 | Lighting and power |  |  | 1 | ls | 5000 | 5000
32 | Increase of chiller size to handle increased incubator flow |  |  | 1 | ls | 40000 | 40000
33 | Heath Incubators |  |  | 16 | stacks | 4000 | 64000
34 | Start tanks, alum. 4X40X3deep |  |  | 20 | ea | 4000 | 80000
35 | 6" Start tank vacuum cleaning pipe to S/F raceways |  |  | 110 | ls | 45 | 4950
|  |  |  | Total for Spring Chinook start tank building |  |  | 533350
MARKUPS AND OTHER DIRECT COSTS
| Subtotal Raw Costs with 15% O& 15% P | [5 empty] | 3863316
| Mobilization/demobilization | [5 empty] | 30000
| Sales Tax @ 9% | [5 empty] | 347698.44
| Contingency @ 30% | [5 empty] | 1158994.8
| Additional Cost at CJDH for Spring Chinook Programs | [5 empty] | 5400009.24
Acclimation Ponds for Spring Programs
Saint Mary's Mission Pond - Modify an existing acclimation pond
| Dewater |  |  | 1 | ls | 3000 | 3000
| Demolition - Remove pond grating and supports |  |  | 1 | ls | 1000 | 1000
| Grading - Fine |  |  | 100 | sy | 4 | 400
| Fencing - Chain Link |  |  | 300 | lf | 15 | 4500
| Fencing - Gate |  |  | 2 | ea | 1100 | 2200
| Fencing - Overhead Netting with supports |  |  | 4000 | sf | 4 | 16000
| Channels - Concrete |  |  | 25 | cy | 600 | 15000
| Channel - Tail and Head Screens |  |  | 2 | ea | 1150 | 2300
| River Intake - Concrete Wing Wall |  |  | 10 | cy | 600 | 6000
| Power - Backup system for Well |  |  | 1 | ls | 3700 | 3700
| Instrumentation & Telemetry - Water level alarm |  |  | 1 | ls | 2700 | 2700
|  |  |  | Total for St. Mary's Mission Pond items |  |  | 56800
Ellisforde Pond - Modifications to an existing 121,500 cubic feet acclimation pond
| Soil Excavation - Excavate, Haul, Dispose |  |  | 100 | cy | 18 | 1800
| Select Fill - Load, Haul, Spread, Compact |  |  | 50 | cy | 61 | 3050
| Grading - Fine |  |  | 100 | sy | 4 | 400
| Pond Liner - 60 mil HDPE |  |  | 100 | sy | 10 | 1000
| Pond Liner - Attachment to Concrete |  |  | 100 | lf | 50 | 5000
| Pipe - Outflow, 24" HDPE |  |  | 300 | lf | 60 | 18000
| Pipe Fittings - Outflow, 24" HDPE |  |  | 4 | ea | 550 | 2200
| Outlet Structure - Concrete |  |  | 25 | cy | 600 | 15000
| Outlet Structure - Screens, 5 FT Wide |  |  | 2 | ea | 1150 | 2300
| Outlet Structure - Stop Logs, 5 FT Wide |  |  | 2 | ea | 1150 | 2300
| Outlet Structure - Slide Gate Valve |  |  | 1 | ea | 3550 | 3550
| Instrumentation & Telemetry - Water level alarm |  |  | 1 | ls | 2700 | 2700
|  |  |  | Total for Ellisforde Pond items |  |  | 57300
| Total, spring Chinook acclimation ponds | [5 empty] | 114100
MARKUPS AND OTHER DIRECT COSTS
| Subtotal Spring Acclimation Pond Costs with 15% O& 15% P | [5 empty] | 114100
| Mobilization/demobilization | [5 empty] | 11410
| Sales Tax @ 9% | [5 empty] | 10269
| Contingency @ 30% | [5 empty] | 34230
| Additional Cost for Ponds for Spring Chinook Programs | [5 empty] | 170009
|  | Total for Spring Chinook Programs with COE supplied water systems | TOTAL for all facilities for the Spring Chinook Programs |  |  |  | 5570018.24
Table XX: SUMMERY CAPITAL CONSTRUCTION COSTS FOR SUMMER/ FALL AND SPRING CHINOOK PROGRAMS
| Total, Summer/Fall Chinook Programs at CJDH with COE supplied rearing water | [5 empty] | 16220361.13
| Total, Summer/fall Chinook Acclimation Ponds | [5 empty] | 1150019.25
|  | TOTAL for Summer/Fall Chinook program |  |  |  |  | 17370380.38
| Additional Cost at CJDH for Spring Chinook Programs | [5 empty] | 5400009.24
| Total, Spring Chinook Acclimation Ponds | [5 empty] | 170009
|  | TOTAL for Spring Chinook program |  |  |  |  | 5570018.24
| Total for both Chinook Programs with COE supplied water systems | [5 empty] | 22940398.62
NOTES:
1. Site piping cost portion attributed to increased pipe sizes due to Spring Chinook program is about $150,000.
2. An item not included in the above cost estimate is an Electric fish directing fence.
3. Well water supply concept based upon information from COE about availability of water in upstream park.