## Slide 1: The Potential for Demand Response to Integrate Variable Energy Resources with the Grid
Pacific Northwest Demand Response Project
January 23rd 2014
Greg Wikler – Navigant Consulting
Ahmad Faruqui – The Brattle Group
Ingrid Rohmund – EnerNOC

## Slide 2: Presentation Overview
  Demand response summary
  Discuss project objectives and task activities
  Identify variable energy resource (VER) growth in the West, highlight associated challenges, and introduce mitigation options (including demand response)
  Demand response resource assessment
    Potential results
    Program options
    Economic assessment framework
  Findings and recommendations

## Slide 3: Demand Response: It is a transforming resource
Commercial Customer
Potential Shortfall
Potential Oversupply
  Historically, demand response (DR) was used to clip peaks in order to ensure system reliability and mitigate price spikes that occurred on an in-frequent and predictable basis
  Now DR is being considered for a wide variety of applications to balance reliability as a result of grid conditions (shortfall, oversupply, frequency) that are increasingly occurring on a frequent and un-predictable basis
Potential Shortfall
Commercial Customer
Time of Day
DR 1.0
DR 2.0
Time of Day

## Slide 4: Project Objectives
  Identify the role that Demand Response (DR) can contribute to mitigate the challenges associated with a growing VER in the Western Interconnection
  Identify DR programs that can meet the needs of VERs
  Describe the various market constructs for which these programs serve
  Define how these programs would be administered
  Develop a framework that will enable more state/province-specific assessments of DR potential for 11 states and 2 provinces
  Different market environments will require different implementation approaches
  This is a planning study and is not intended to be an implementation guide

## Slide 5: Major Contributors to VER: Solar and Wind Resources Renewable Energy Shares in the Western Interconnection by 2022
Source: WECC 2022 PC1 Common Case document; July 25, 2013
  Overall Renewable:
  168,987 GWh
(16.6% of total generation)
  61.25 GW
  (22.4% of total capacity)
  Wind Share in Renewable:
  91,253 GWh (54%)
  34.7 GW (57%)
  Estimated Solar Share:
  23,658 GWh (14%)
  19.7 GW (32%)
Variable
Renewable
Non-Variable
Renewable
BC
AL
WA
ID
OR
MT
WY
CO
UT
AZ
NM
CA
NV
Assumed capacity factors by resource type:
Wind-30%
Solar-13.7%

## Slide 6: Challenges with a Growing VER Portfolio
  These challenges are typically addressed by “backfilling” the renewable resource with different types of generation or storage options, including Demand Response
Variability in VER production | Aggregate output form renewable energy resources is drastically changing system load availability
Forecast uncertainties | All types of forecasts (wind and solar) are subject to inaccuracies
Ramping characteristics | VERs tend to have large and very steep and rapid ramps that are difficult to forecast
Over generation from VERs | Wind resources are likely to be more abundant at night (particularly in wind-rich-rich regions such as PNW and mountain states) during times of limited demand, leading to over-generation and thus grid reliability challenges

## Slide 7: There are several options to mitigate the effects of VER but no one “silver bullet” solution
  The magnitude and economic viability of all options should be assessed
  Interstate transfers should also be assessed to correct load imbalances caused by VERs
  Demand Response works within the Distributed Storage set of options
Traditional Generation
gas turbines, coal plants
Centralized Storage
pump storage hydro, compressed air, battery
Distributed Storage
water heaters, thermal storage, process loads, EVs

## Slide 8: DR 2.0 has the potential to mitigate the effects of VER
  But DR needs to be fast, swift and predictable
  Customer loads must be equipped with automation equipment
  Customer loads must be available 24x7 year round
  Customer loads must be measured on a frequent basis
  Customer loads must be capable of moving in both directions
  Different DR product types are needed to address VER integration challenges
  Contingency
  Regulation
  Load following
  Existing DR programs can be repurposed to meet the new challenges
  Legacy utility DR programs (DLC, Interruptible, Load Aggregator)
  Ancillary services with RTOs (ERCOT, PJM)
  Fast DR and load following pilots (PG&E, BPA, Hawaiian Electric)

## Slide 9: Demand Response Potential Methodological Approach
  Establish baseline end-use load characteristics
  Determine technical potential
  Determine achievable potential
  Develop DR programs and approaches for VER integration
  Determine economic potential of the DR programs

## Slide 10: DR Potential Analysis Framework
Estimate total potential MW by day-type, state/province, sector, segment, and end-use
Develop 8760 (weather normal) End-Use Load shapes by segment, building-type, end-use, and census region
Unitize all 8760 shapes by state/province, sector, segment and end use; scale appropriately using control totals over the forecast horizon
Apply multiple factors (technical & achievable) to estimate the portion of load available for DR by end-use and segment. These factors are based on available literature on the topic
Create state/province level segment and end-use level shapes based on mix of building-types in that state/province
Step 4:
Estimate Technical and Achievable Potentials
Step 3:
Apply Factors
Step 2:
Develop Baseline Forecast
Step 1:
Customize Load Shapes
Foundation:
End-Use Data

## Slide 11: Commercial and Residential Sectors Dominate in Potential DR Resource Availability
Aggregate DR Potential on a Typical Summer Weekday in 2020
Chart: DR Potential (MW)
| Load Dec. | Load Dec. | Load Inc. | Load Dec. | Load Inc. | Contingency |  | Regulation |  | Load Following
Residential | 994.9379 | 994.9379 | -34.6227 | 994.9379 | -34.6227
Commercial | 1667.66 | 474.1215 | -247.8166 | 1303.9656 | -717.6021
Industrial | 516.5119 | 217.8905 | 0 | 243.1035 | -4.637
Total Potential (% of Load) | 0.056041 | 0.029737 | -0.0049788 | 0.04481 | -0.013342

## Slide 12: Seasonal Variations in DR Potential Availability
Typical Summer Weekday in 2020
Typical Winter Weekday in 2020
Typical Spring Weekday in 2020
Typical Fall Weekday in 2020
Chart: DR Potential (MW)
| Load Dec. | Load Dec. | Load Inc. | Load Dec. | Load Inc. | Contingency |  | Regulation |  | Load Following
Residential | 994.9379 | 994.9379 | -34.6227 | 994.9379 | -34.6227
Commercial | 1667.66 | 474.1215 | -247.8166 | 1303.9656 | -717.6021
Industrial | 516.5119 | 217.8905 | 0 | 243.1035 | -4.637
Total Potential (% of Load) | 0.056041 | 0.029737 | -0.0049788 | 0.04481 | -0.013342
Chart: DR Potential (MW)
| Load Dec. | Load Dec. | Load Inc. | Load Dec. | Load Inc. | Contingency |  | Regulation |  | Load Following
Residential | 135.5156 | 135.5156 | -65.9063 | 135.5156 | -65.9063
Commercial | 1075.3537 | 313.2583 | -91.9998 | 807.18 | -241.3608
Industrial | 334.2825 | 217.8905 | 0 | 243.1035 | -4.637
Total Potential (% of Load) | 0.035616 | 0.015367 | -0.0036398 | 0.027333 | -0.0071894
Chart: DR Potential (MW)
| Load Dec. | Load Dec. | Load Inc. | Load Dec. | Load Inc. | Contingency |  | Regulation |  | Load Following
Residential | 394.617 | 394.617 | -58.5182 | 394.617 | -58.5182
Commercial | 1373.5 | 382.6949 | -168.9368 | 1021.1261 | -476.0395
Industrial | 483.8245 | 217.8905 | 0 | 243.1035 | -4.637
Total Potential (% of Load) | 0.047386 | 0.020941 | -0.0047861 | 0.034906 | -0.011346
Chart: DR Potential (MW)
| Load Dec. | Load Dec. | Load Inc. | Load Dec. | Load Inc. | Contingency |  | Regulation |  | Load Following
Residential | 148.9165 | 148.9165 | -72.8461 | 148.9165 | -72.8461
Commercial | 1031.368 | 299.6602 | -69.852 | 760.5361 | -171.8181
Industrial | 330.2122 | 217.8905 | 0 | 243.1035 | -4.637
Total Potential (% of Load) | 0.033077 | 0.014595 | -0.0031248 | 0.025239 | -0.0054593

## Slide 13: Average Hourly Load Reduction Profiles for Contingency Services
Typical Summer Weekday in 2020
Typical Winter Weekday in 2020
Typical Spring Weekday in 2020
Typical Fall Weekday in 2020
Chart: Load Reduction Potential (MW)
| 0 | 4.1666666666666699E-2 | 8.3333333333333343E-2 | 0.125 | 0.16666666666666688 | 0.20833333333333323 | 0.25 | 0.29166666666666741 | 0.33333333333333298 | 0.37500000000000028 | 0.41666666666666741 | 0.45833333333333293 | 0.5 | 0.54166666666666696 | 0.58333333333333259 | 0.62500000000000056 | 0.66666666666666752 | 0.70833333333333304 | 0.75000000000000056 | 0.79166666666666696 | 0.83333333333333304 | 0.87500000000000056 | 0.91666666666666696 | 0.95833333333333304
Residential | 109.5988 | 97.4514 | 91.0899 | 97.332 | 121.5498 | 163.0728 | 199.5047 | 218.7707 | 216.6516 | 192.31 | 167.2691 | 150.5011 | 136.6881 | 129.5442 | 126.738 | 127.3904 | 135.5344 | 148.0075 | 161.5789 | 172.2423 | 174.0604 | 164.6211 | 145.9315 | 126.5562
Commercial | 730.8697 | 705.6694 | 707.1091 | 731.4684 | 764.2391 | 816.2366 | 900.996 | 1008.8286 | 1114.0782 | 1201.9276 | 1251.0286 | 1271.3365 | 1289.834 | 1305.9582 | 1314.3178 | 1307.983 | 1283.2413 | 1242.3043 | 1180.2531 | 1097.1303 | 1005.5827 | 916.2689 | 834.7233 | 771.4465
Industrial | 313.2735 | 322.3842 | 320.6884 | 320.6927 | 321.0173 | 332.6185 | 341.4414 | 348.8837 | 356.3284 | 349.4892 | 344.8133 | 342.2654 | 343.9574 | 351.7969 | 346.2124 | 338.8134 | 325.5124 | 319.206 | 314.2989 | 314.6876 | 316.2601 | 314.4759 | 314.8279 | 311.1481
Total | 1979.4722 | 1842.2299 | 1749.8739 | 1718.3432 | 1765.5931 | 1930.9497 | 2220.5334 | 2569.1006 | 2926.5031 | 3249.7627 | 3558.2894 | 3875.5163 | 4187.7513 | 4515.8253 | 4766.3924 | 4906.4617 | 4880.4578 | 4657.4476 | 4267.8964 | 3796.7414 | 3319.9716 | 2881.6786 | 2518.2917 | 2213.5502
Chart: Load Reduction Potential (MW)
| 0 | 4.1666666666666699E-2 | 8.3333333333333343E-2 | 0.125 | 0.16666666666666688 | 0.20833333333333323 | 0.25 | 0.29166666666666741 | 0.33333333333333298 | 0.37500000000000028 | 0.41666666666666741 | 0.45833333333333293 | 0.5 | 0.54166666666666696 | 0.58333333333333259 | 0.62500000000000056 | 0.66666666666666752 | 0.70833333333333304 | 0.75000000000000056 | 0.79166666666666696 | 0.83333333333333304 | 0.87500000000000056 | 0.91666666666666696 | 0.95833333333333304
Residential | 258.8779 | 217.6994 | 181.8334 | 168.2723 | 178.4281 | 211.5948 | 245.6943 | 270.0592 | 284.901 | 292.1417 | 316.177 | 366.0872 | 430.145 | 505.6913 | 583.0184 | 645.0972 | 681.6808 | 682.4932 | 648.3374 | 595.1479 | 530.9936 | 461.9311 | 392.595 | 321.9102
Commercial | 791.4634 | 783.8463 | 802.3404 | 833.9963 | 893.0476 | 1000.8902 | 1157.7111 | 1338.6059 | 1519.8256 | 1667.993 | 1778.1044 | 1867.7092 | 1937.6984 | 1983.4118 | 1998.0537 | 1974.2298 | 1901.9401 | 1771.8555 | 1591.3992 | 1388.5032 | 1195.0988 | 1032.5821 | 914.0764 | 839.6186
Industrial | 425.2724 | 433.5285 | 429.9686 | 424.9981 | 425.1889 | 431.7905 | 466.6007 | 518.2646 | 537.3872 | 547.6029 | 548.6304 | 547.2082 | 540.2638 | 556.3792 | 543.6525 | 528.2083 | 509.3664 | 483.4588 | 460.244 | 454.9171 | 459.4644 | 453.5048 | 444.3948 | 441.492
Total | 1979.4722 | 1842.2299 | 1749.8739 | 1718.3432 | 1765.5931 | 1930.9497 | 2220.5334 | 2569.1006 | 2926.5031 | 3249.7627 | 3558.2894 | 3875.5163 | 4187.7513 | 4515.8253 | 4766.3924 | 4906.4617 | 4880.4578 | 4657.4476 | 4267.8964 | 3796.7414 | 3319.9716 | 2881.6786 | 2518.2917 | 2213.5502
Chart: Load Reduction Potential (MW)
| 0 | 4.1666666666666699E-2 | 8.3333333333333343E-2 | 0.125 | 0.16666666666666688 | 0.20833333333333323 | 0.25 | 0.29166666666666741 | 0.33333333333333298 | 0.37500000000000028 | 0.41666666666666741 | 0.45833333333333293 | 0.5 | 0.54166666666666696 | 0.58333333333333259 | 0.62500000000000056 | 0.66666666666666752 | 0.70833333333333304 | 0.75000000000000056 | 0.79166666666666696 | 0.83333333333333304 | 0.87500000000000056 | 0.91666666666666696 | 0.95833333333333304
Residential | 669.6345 | 546.7445 | 451.4357 | 398.9387 | 379.8619 | 393.513 | 421.418 | 461.8092 | 519.7508 | 602.1005 | 733.1465 | 917.2127 | 1136.765 | 1377.5906 | 1613.2119 | 1799.1606 | 1898.0998 | 1883.8305 | 1760.6259 | 1576.3125 | 1370.8599 | 1169.4627 | 989.7085 | 807.3154
Commercial | 862.9429 | 839.9151 | 849.2318 | 877.0336 | 944.2405 | 1085.4849 | 1306.2587 | 1571.0766 | 1841.0677 | 2065.73 | 2233.0715 | 2365.4023 | 2466.8249 | 2534.1477 | 2559.2074 | 2529.0136 | 2429.624 | 2249.8031 | 2001.3163 | 1723.4557 | 1457.2672 | 1229.9896 | 1058.3804 | 943.3537
Industrial | 446.8948 | 455.5702 | 449.2063 | 442.3709 | 441.4907 | 451.9518 | 492.8567 | 536.2147 | 565.6846 | 581.9322 | 592.0714 | 592.9012 | 584.1614 | 604.087 | 593.9731 | 578.2874 | 552.7341 | 523.814 | 505.9541 | 496.9732 | 491.8445 | 482.2263 | 470.2028 | 462.8811
Chart: Load Reduction Potential (MW)
| 0 | 4.1666666666666699E-2 | 8.3333333333333343E-2 | 0.125 | 0.16666666666666688 | 0.20833333333333323 | 0.25 | 0.29166666666666741 | 0.33333333333333298 | 0.37500000000000028 | 0.41666666666666741 | 0.45833333333333293 | 0.5 | 0.54166666666666696 | 0.58333333333333259 | 0.62500000000000056 | 0.66666666666666752 | 0.70833333333333304 | 0.75000000000000056 | 0.79166666666666696 | 0.83333333333333304 | 0.87500000000000056 | 0.91666666666666696 | 0.95833333333333304
Residential | 92.7046 | 82.9444 | 75.8813 | 80.2615 | 100.0374 | 135.7639 | 169.8972 | 190.186 | 191.3618 | 173.6844 | 154.7085 | 142.3119 | 133.2404 | 128.393 | 127.4877 | 130.9151 | 139.5614 | 149.4435 | 156.734 | 159.1409 | 154.9009 | 144.2098 | 127.3858 | 111.2195
Commercial | 722.4626 | 703.8889 | 711.0039 | 736.8539 | 774.8119 | 837.7383 | 934.6873 | 1053.1683 | 1170.9179 | 1269.8911 | 1334.7781 | 1375.8358 | 1409.4638 | 1432.5135 | 1437.0765 | 1416.3694 | 1370.5042 | 1302.8269 | 1213.6538 | 1110.0756 | 1004.3435 | 905.2256 | 820.749 | 759.65
Industrial | 319.5278 | 326.8619 | 325.1634 | 324.2798 | 325.3378 | 340.1484 | 347.5634 | 352.7587 | 356.7221 | 351.1952 | 347.1064 | 345.9998 | 348.6825 | 356.0916 | 349.4318 | 339.9252 | 330.7407 | 325.411 | 318.3278 | 318.7021 | 318.2489 | 318.7721 | 319.0616 | 316.7192
Total | 1979.4722 | 1842.2299 | 1749.8739 | 1718.3432 | 1765.5931 | 1930.9497 | 2220.5334 | 2569.1006 | 2926.5031 | 3249.7627 | 3558.2894 | 3875.5163 | 4187.7513 | 4515.8253 | 4766.3924 | 4906.4617 | 4880.4578 | 4657.4476 | 4267.8964 | 3796.7414 | 3319.9716 | 2881.6786 | 2518.2917 | 2213.5502

## Slide 14: Aggregate DR Potential by State/Province in 2020
Typical Summer Weekday ‘Load Following’ Potential
Total Load Decrease Potential- 2,542 MW
Total Load Increase Potential- 757 MW
Chart: 
| AB | AZ | BC | CA | CO | ID | MT | NM | NV | OR | UT | WA | WY
Load Decrease | 115.3416 | 562.788 | 118.6649 | 852.8792 | 144.3905 | 50.624 | 36.7673 | 98.2528 | 138.8265 | 106.8554 | 75.397 | 211.2823 | 29.9376
Chart: 
| AB | AZ | BC | CA | CO | ID | MT | NM | NV | OR | UT | WA | WY
Load Increase | 54.6807 | 74.3486 | 50.7821 | 251.2491 | 66.3375 | 20.5103 | 16.4456 | 22.4582 | 22.336 | 47.8209 | 26.136 | 89.5866 | 14.1702

## Slide 15: DR Potential Load Decrease by State/Province Shares in the Western Interconnection Potential
“Load Following” Potential for a Typical Summer Weekday in 2020
  Total Load Decrease Potential- 2,542 MW
    Residential: 995 MW
    Commercial: 1,304 MW
    Industrial: 243 MW
4.7%
5.5%
1.4%
1.2%
2.0%
5.7%
8.3%
4.2%
3.0%
3.9%
21.1%
34%
4.5%
Chart: 
 | 13.0297 | 86.9142 | 15.3977
Chart: 
 | 27.1391 | 75.7416 | 15.7842

## Slide 16: DR Potential Load Increase by State/Province Shares in the Western Interconnection Potential
“Load Following” Potential for a Typical Summer Weekday in 2020
  Total Load Increase Potential- 757 MW
    Residential: 35 MW
    Commercial: 718 MW
    Industrial: 5 MW
6.7%
3.0%
2.2%
1.9%
2.7%
8.8%
11.8%
6.3%
3.5%
3.0%
9.8%
33%
7.2%

## Slide 17: Residential Sector Potential is Dominated by Cooling Load
Residential Sector Potential on a Typical Summer Weekday in 2020
Chart: DR Potential (MW)
| Load Dec. | Load Dec. | Load Inc. | Load Dec. | Load Inc. | Contingency |  | Regulation |  | Load Following
Cooling | 922.2489 | 922.2489 | 0 | 922.2489 | 0
Heating | 1.1448 | 1.1448 | -0.44361 | 1.1448 | -0.44361
Water Heating | 71.5442 | 71.5442 | -34.1791 | 71.5442 | -34.1791
Residential | 0.07654 | 0.07654 | -0.0026635 | 0.07654 | -0.0026635

## Slide 18: Residential DR Potential Varies by Available End-uses Across Seasons
Typical Summer Weekday Potential in 2020
Typical Winter Weekday Potential in 2020
Typical Spring Weekday Potential in 2020
Typical Fall Weekday Potential in 2020

## Slide 19: Residential: Hourly Load Reduction Profiles for Contingency Services
Typical Summer Weekday Profile in 2020
Typical Winter Weekday Profile in 2020
Typical Spring Weekday Profile in 2020
Typical Fall Weekday Potential in 2020

## Slide 20: Commercial Sector Potential Availability is Dominated by Retail and Large Office Buildings
Commercial Sector Potential on a Typical Summer Weekday in 2020
Chart: DR Potential (MW)
| Load Dec. | Load Dec. | Load Inc. | Load Dec. | Load Inc. | Contingency |  | Regulation |  | Load Following
Food Service | 162.4506 | 23.2153 | -11.2229 | 66.0711 | -33.1846
Large Office | 374.0917 | 114.3299 | -20.6019 | 310.2389 | -58.147
Public Assembly | 209.0422 | 60.3159 | -48.5559 | 177.5746 | -145.4626
Ref. Warehouse | 22.5925 | 1.2934 | -0.82019 | 3.4534 | -2.4606
Retail | 620.7652 | 187.7159 | -122.2561 | 502.93 | -350.3931
School | 278.7179 | 87.2511 | -44.3596 | 243.6975 | -127.9542
Commercial | 0.04958 | 0.014096 | -0.0073677 | 0.038768 | -0.021335

## Slide 21: Seasonal Variations in Commercial DR Potential Availability
Typical Summer Weekday Potential in 2020
Typical Winter Weekday Potential in 2020
Typical Spring Weekday Potential in 2020
Typical Fall Weekday Potential in 2020
Chart: DR Potential (MW)
| Load Dec. | Load Dec. | Load Inc. | Load Dec. | Load Inc. | Contingency |  | Regulation |  | Load Following
Food Service | 162.4506 | 23.2153 | -11.2229 | 66.0711 | -33.1846
Large Office | 374.0917 | 114.3299 | -20.6019 | 310.2389 | -58.147
Public Assembly | 209.0422 | 60.3159 | -48.5559 | 177.5746 | -145.4626
Ref. Warehouse | 22.5925 | 1.2934 | -0.82019 | 3.4534 | -2.4606
Retail | 620.7652 | 187.7159 | -122.2561 | 502.93 | -350.3931
School | 278.7179 | 87.2511 | -44.3596 | 243.6975 | -127.9542
Commercial | 0.04958 | 0.014096 | -0.0073677 | 0.038768 | -0.021335
Chart: DR Potential (MW)
| Load Dec. | Load Dec. | Load Inc. | Load Dec. | Load Inc. | Contingency |  | Regulation |  | Load Following
Food Service | 151.0792 | 19.344 | -7.9108 | 54.3698 | -23.2086
Large Office | 340.2317 | 103.7978 | -19.3922 | 277.4207 | -53.9978
Public Assembly | 158.8811 | 44.3411 | -34.0195 | 129.5955 | -101.8257
Ref. Warehouse | 22.1618 | 1.0956 | -0.17326 | 2.86 | -0.51977
Retail | 481.5991 | 145.0918 | -75.604 | 369.7345 | -207.2494
School | 219.5472 | 69.0246 | -31.8371 | 187.1456 | -89.2382
Commercial | 0.046324 | 0.012907 | -0.0056977 | 0.034439 | -0.016055
Chart: DR Potential (MW)
| Load Dec. | Load Dec. | Load Inc. | Load Dec. | Load Inc. | Contingency |  | Regulation |  | Load Following
Food Service | 119.6292 | 15.5386 | -4.0018 | 42.8155 | -11.4177
Large Office | 284.6892 | 90.243 | -11.5857 | 235.705 | -29.9252
Public Assembly | 102.2604 | 28.1166 | -14.3725 | 80.8351 | -42.8407
Ref. Warehouse | 18.1173 | 1.0449 | -0.002219 | 2.7078 | -0.0066569
Retail | 351.9578 | 113.6838 | -27.1045 | 267.2601 | -56.8197
School | 154.7142 | 51.0334 | -12.7854 | 131.2126 | -30.8083
Commercial | 0.037687 | 0.01095 | -0.0025524 | 0.02779 | -0.0062783
Chart: DR Potential (MW)
| Load Dec. | Load Dec. | Load Inc. | Load Dec. | Load Inc. | Contingency |  | Regulation |  | Load Following
Food Service | 119.9696 | 16.1655 | -4.7723 | 44.8113 | -13.7742
Large Office | 293.1585 | 92.8286 | -13.8499 | 244.5778 | -37.101
Public Assembly | 110.885 | 30.9264 | -18.6995 | 89.3548 | -55.8435
Ref. Warehouse | 17.7483 | 1.0338 | -0.025587 | 2.683 | -0.07676
Retail | 366.6489 | 117.6356 | -36.7633 | 282.5095 | -87.727
School | 166.9435 | 54.6683 | -17.8892 | 143.2436 | -46.8383
Commercial | 0.039902 | 0.011624 | -0.0034137 | 0.029951 | -0.0089558

## Slide 22: Commercial: Hourly Load Reduction Profiles for Contingency Services
Typical Summer Weekday Profile in 2020
Typical Winter Weekday Profile in 2020
Typical Spring Weekday Profile in 2020
Typical Fall Weekday Profile in 2020

## Slide 23: Water/Wastewater Treatment Plants and Ag Pumping Dominate Industrial Potential Availability
Industrial Sector Potential on a Typical Summer Weekday in 2020
Chart: DR Potential (MW)
| Load Dec. | Load Dec. | Load Inc. | Load Dec. | Load Inc. | Contingency |  | Regulation |  | Load Following
Ag Pumping | 273.4084 | 0 | 0 | 0 | 0
Data Centers | 217.8905 | 217.8905 | 0 | 217.8905 | 0
Water Wastewater | 25.213 | 0 | 0 | 25.213 | -4.637
Industrial | 0.051169 | 0.021586 | 0 | 0.024083 | -0.00045937

## Slide 24: Seasonal Variations in Industrial DR Potential
Typical Summer Weekday Potential in 2020
Typical Winter Weekday Potential in 2020
Typical Spring Weekday Potential in 2020
Typical Fall Weekday Potential in 2020
Chart: DR Potential (MW)
| Load Dec. | Load Dec. | Load Inc. | Load Dec. | Load Inc. | Contingency |  | Regulation |  | Load Following
Ag Pumping | 87.1087 | 0 | 0 | 0 | 0
Data Centers | 217.8905 | 217.8905 | 0 | 217.8905 | 0
Water Wastewater | 25.213 | 0 | 0 | 25.213 | -4.637
Industrial | 0.037303 | 0.024614 | 0 | 0.027462 | -0.00052382
Chart: DR Potential (MW)
| Load Dec. | Load Dec. | Load Inc. | Load Dec. | Load Inc. | Contingency |  | Regulation |  | Load Following
Ag Pumping | 240.721 | 0 | 0 | 0 | 0
Data Centers | 217.8905 | 217.8905 | 0 | 217.8905 | 0
Water Wastewater | 25.213 | 0 | 0 | 25.213 | -4.637
Industrial | 0.048988 | 0.022062 | 0 | 0.024615 | -0.00046951
Chart: DR Potential (MW)
| Load Dec. | Load Dec. | Load Inc. | Load Dec. | Load Inc. | Contingency |  | Regulation |  | Load Following
Ag Pumping | 273.4084 | 0 | 0 | 0 | 0
Data Centers | 217.8905 | 217.8905 | 0 | 217.8905 | 0
Water Wastewater | 25.213 | 0 | 0 | 25.213 | -4.637
Industrial | 0.051169 | 0.021586 | 0 | 0.024083 | -0.00045937
Chart: DR Potential (MW)
| Load Dec. | Load Dec. | Load Inc. | Load Dec. | Load Inc. | Contingency |  | Regulation |  | Load Following
Ag Pumping | 91.179 | 0 | 0 | 0 | 0
Data Centers | 217.8905 | 217.8905 | 0 | 217.8905 | 0
Water Wastewater | 25.213 | 0 | 0 | 25.213 | -4.637
Industrial | 0.037647 | 0.024539 | 0 | 0.027378 | -0.00052222

## Slide 25: Industrial: Hourly Load Reduction Profiles for Contingency Services
Typical Summer Weekday Profile in 2020
Typical Winter Weekday Profile in 2020
Typical Spring Weekday Profile in 2020
Typical Fall Weekday Profile in 2020

## Slide 26: High Participation Scenario Analysis
  We ran a sensitivity analysis under higher participation level assumptions, as compared to the “base” scenario.
  Participation rates are assumed to be 1.5 to 2 times “base” scenario participation levels.
  Scenario assumed to be driven by aggressive efforts to market and deploy DR 2.0 programs to end-use customers.
  This scenario could also be spurred by rapid decline in technology enablement costs, thereby accelerating adoption by customers.
  Comparison of results shows that the overall load curtailment potential increase ranges from ~30-55%, as compared to the base scenario.

## Slide 27: Base and High Participation Level Potential Estimates Comparison
Aggregate DR Potential on a Typical Summer Weekday in 2020
Chart: DR Potential (MW)
| Base | High Part. | Base | High Part. | Base | High Part. | Base | High Part. | Base | High Part. | Contingency |  | Regulation |  | Load Following
Residential | 994.9379 | 1954.1037 | 994.9379 | 1492.9793 | -34.6227 | -52.1559 | 994.9379 | 1511.4242 | -34.6227 | -52.1559
Commercial | 1667.66 | 2235.4126 | 474.1215 | 899.4748 | -247.8166 | -469.9785 | 1303.9656 | 1828.2781 | -717.6021 | -1051.2846
Industrial | 516.5119 | 665.8225 | 217.8905 | 217.8905 | 0 | 0 | 243.1035 | 255.71 | -4.637 | -6.9555
 | 0.056041 | 0.085589 | 0.029737 | 0.046014 | -0.0049788 | -0.0092041 | 0.04481 | 0.063379 | -0.013342 | -0.019574

## Slide 28: DR 1.0 vs. DR 2.0 Potential Estimates
  Estimated DR 1.0 Potential in 11 WECC states
  13.6 GW in 2022
  Ref: WECC 20-year Demand Response Forecast. Prepared by the Brattle Group for Lawrence Berkeley National Laboratory, June 2012
  Estimated DR 2.0 Potential in 11 WECC states (Potential Load Decrease in ‘Load Following Product’)
  2.3 GW in 2022 (Base Scenario)
  3.3 GW in 2022 (High Participation Scenario)
  DR 2.0 Potential as a % of DR 1.0 Potential in 11 WECC states
  ~17% (Base Scenario)
  ~24% (High Participation Scenario)

## Slide 29: Reshaping the "Duck Chart” through DR?
Chart: Net Load (MW)
| 0 | 4.1666666666666699E-2 | 8.3333333333333343E-2 | 0.125 | 0.16666666666666688 | 0.20833333333333343 | 0.25 | 0.29166666666666785 | 0.33333333333333298 | 0.37500000000000061 | 0.41666666666666785 | 0.45833333333333293 | 0.5 | 0.54166666666666696 | 0.58333333333333259 | 0.62500000000000133 | 0.66666666666666763 | 0.70833333333333304 | 0.75000000000000133 | 0.79166666666666696 | 0.83333333333333304 | 0.87500000000000133 | 0.91666666666666696 | 0.95833333333333304
Net load w/o DR | 21500 | 20000 | 18700 | 18200 | 18100 | 18300 | 18300 | 18050 | 17700 | 15300 | 13300 | 12500 | 12000 | 11650 | 11300 | 11250 | 11550 | 13500 | 18000 | 23800 | 25100 | 23850 | 22200 | 21000
Net load with DR | 21500 | 20151.3664 | 18854.0583 | 18349.6751 | 18242.7799 | 18433.1388 | 18419.2452 | 18152.6023 | 17788.0813 | 15375.2735 | 13365.7947 | 12558.9452 | 12050.1053 | 11692.1187 | 11337.5932 | 11288.2534 | 11593.5191 | 12832.4806 | 17355.9468 | 23188.7487 | 24526.9366 | 23317.7175 | 21705.6064 | 20534.7779
CAISO “Net Load Curve” for March 27, 2020
Illustration of the Potential Implications of DR Integration on Net Load (CA Example)
  Average DR Potential Impacts on Net Load for a Typical Winter Weekday
    Load Decrease Potential (% of “Net Load”)~4%
    Load Increase Potential (% of “Net Load”)~0.5%
Please note that the “net load” curve with DR is estimated using average winter weekday load profile for CA, and not specifically for the month of March and on the 27th day of the month
This chart is for illustration purposes only, and does not represent the actual CAISO load data. It is meant to illustrate the relative magnitude of the DR potential estimates vis-à-vis the “net load”.

## Slide 30: DR Program Considerations
  A new generation of DR programs can possibly help realize the potential opportunities for addressing VER integration challenges
  Additionally, existing DR programs could also be modified and positioned to address VER integration challenges
  These DR programs will need to embody characteristics such as:
    Responding to events with short notification periods
    Responding to a relatively high frequency of DR events
    Capable of providing bi-directional response
    Sustaining load reductions over relatively long time periods
  Automated response with advanced control and communication capabilities will be a key component of program design
  Program designs will need to take into consideration customer segments and end-uses that are being targeted.
    Frequent starts and stops will have an impact on processes, maintenance and lifetime of equipment and this will need to be addressed
    Impacts on customer electricity bills, caused by load increase, will also need to be considered
    Appropriate incentive levels will need to be designed

## Slide 31: DR Program Considerations (continued)
  Opportunities exist to leverage the customer base enrolled in traditional DR program offerings offered by utilities across western states.
  Existing residential and small commercial direct load control (DLC) type programs could serve as a base from which to further build upon
  Targeted loads include air-conditioning, space heating, and water heating
  Advanced DLC technologies will enhance performance and include smart appliances
  Irrigation loads are increasingly becoming an attractive target for advanced DLC applications
  Western states with significant DLC programs include California, Colorado, Idaho, New Mexico, Nevada, and Utah
  Existing commercial and industrial curtailment type programs could serve as a base from which to further build upon
  Targeted loads include HVAC, lighting and industrial processes
  Utilization of automated controls and advanced communication systems will be necessary to ensure performance
  An aggregated portfolio of customers is likely to help fulfill essential program attributes
  Western states with sizeable C&I participation base in DR options are- Arizona, California, Colorado, New Mexico, Nevada, Oregon, and Washington

## Slide 32: DR Potential: Assessing the Economic Viability
  Data and methodology gaps limit our ability to thoroughly assess the economic potential of the DR options
  Data about the size and cost of the various VER integration options is limited
  No cost effectiveness methods currently exist to assess VER options
  Key questions:
  What are the costs associated with the DR programs?
  What is the right value for the DR products that are integrated with VER?
  What is the resource to be avoided for load reductions and load increases?
  Are the standard practice approaches for DR cost-effectiveness appropriate for VER resource integration?

## Slide 33: Cost Effectiveness Framework
  DR program cost elements
  Program implementation and operations
  Enablement costs for automation equipment and telemetry
  Customer incentives (capacity and energy)
  DR program benefit elements
  Load reductions: Avoid the investment in traditional generation resources, such as a peaking plants
  Load building: Avoid the investment in special equipment designed to mitigate the effects of overproduction of electricity on the grid
    Consider potential benefits associated with additional revenue to renewable energy developers

## Slide 34: Findings and Recommendations
  Findings:
      DR 2.0 will play an important role in mitigating the effects of VER in the next decade
      There are a limited number of customer segments and end-use loads that can accommodate the needs for VER integration
      Utilities can adapt existing several existing DR programs to meet the technical requirements for VER integration
      DR is one of many options to mitigate the effects of VER
  Recommendations:
Develop the necessary parameters to support a meaningful analysis of DR cost-effectiveness of for VER integration
Identify the magnitude and economic viability for all options that can mitigate the effects of VER
Utilities and balancing authorities in the Western Interconnection should begin developing their own estimates of DR potential for VER integration
Develop pilot programs to improve the quantification of DR potential and test new breakthrough technologies

## Slide 35: Appendix Slides
  Definitions of Ancillary Services Product Types
  States and Provinces Included in the Study

## Slide 36: Ancillary Services Products Definitions and Attributes
Source: Perlstein et al, “Potential Role of DR Resources in Maintaining
Grid Stability and Integrating Variable Renewable Energy”, July 2012.
Spinning Reserves- The California ISO defines spinning reserves as follows- “Spinning reserve is the portion of unloaded capacity from units already connected or synchronized to the grid and that can deliver their energy in 10 minutes and run for at least two hours.” (Source- Perlstein et.al., 2012)
Non-spinning Reserves- The California ISO defines non-spinning reserves as follows- “Non-spinning (or supplemental) reserve is the extra generating capacity that is not currently connected or synchronized to the grid but that can be brought online and ramp up to a specified load within ten minutes.” (Source- Perlstein et.al., 2012)
Regulation- The California ISO defines regulation as follows- “Regulation energy is used to control system frequency that can vary as generators access the system and must be maintained very narrowly around 60 hertz. Units and system resources providing regulation are certified by the ISO and must respond to ‘automatic generation control’ (AGC) signals to increase or decrease their operating levels depending upon the service being provided, regulation up or regulation down.” (Source- Perlstein et.al., 2012).
Load Following- The California ISO defines load following as- “Load following is the ramping capability of a resource to match the maximum megawatts by which the net load is expected to change in either an upward or a downward direction in a given hour in a given month...” (Source- Perlstein et.al., 2012).
Attribute | Spinning/non-spinning reserve | Regulation | Continuous ramping/load following
Telemetry | Required | Required | Required
Response time | <10 minute; <10 second to begin ramping is desirable | <1 minute | <1hour
Automated response | Required | Required | Required
Event limitations | Dozens to more than 100 events, lasting at least 1 hour each | Continuous availability desired | 10 hours or more duration, minimum of one hour
Daily/seasonal availability | 24x7 year round | 24x7 year round | 24x7 year round, with seasonal variation
Target end uses | Agricultural and municipal water pumping, electric water heating | Temperature controlled warehouses, industrial motor load on Variable Frequency Drives (VFDs) | Commercial Lighting and HVAC
DR Program Attributes Required to Provide Products Capable of Supporting Integration of Variable Generation Resources

## Slide 37: States and Provinces Included in the Study
  States
  Arizona, California, Colorado, Idaho, Montana, New Mexico, Nevada, Oregon, Utah, Washington, and Wyoming.
  Provinces
  Alberta, British Columbia