Summary of NEEM™ Manufactured Home Field Data

(1997-98 Sitings in Idaho and Washington)

Bob Davis

### Alison Roberts

David Baylon

Draft

### November, 2000

Prepared for the Idaho Department of

Water Resources – Energy Division

Ken Eklund, Project Manager

###### Introduction

In April and May 2000, a random sample of manufactured homes built to the Northwest Energy Efficient Manufactured Home™ Standards and sited in Idaho and Washington during 1997-98 were visited and evaluated.  Field technicians from Delta T, Inc. (Alan Van Zuuk and Bruce Manclark), WSU Cooperative Extension Energy Program (David Hales), and the Idaho Energy Division (Ingo Stroup) assessed the quality of home set-up (structural and operational issues), and tested house and duct tightness, system airflow, and performance of the whole-house ventilation system.  The study employed most of the protocol used for the 1993 evaluation of the Manufactured Housing Acquisition Program (MAP).  That study was much larger (162 sites) and included homes from all four states in Bonneville Power Administration’s (BPA) service territory.  The homeowner survey was omitted and additional tests for HVAC system airflow and operating static pressure were added.

## Basic Sample Characteristics

|  | Idaho % | Washington % | Both States % | MAP Homes (1994 study) |
| --- | --- | --- | --- | --- |
| Double section home | 80 | 67 | 73 | 81.5 |
| Triple section home | 20 | 33 | 27 | 6.7 |
| Home size (sq. ft) | 1,648 | 1,856 | 1,750 | 1,433 |

This study includes 25 homes from Idaho and 24 from Washington.  This size of random sample should be viewed as an absolute minimum from which to generalize.  Some general sample characteristics are worth noting.  There were more triple section homes than in the MAP study and no single section homes, thus average home size was considerably greater.  (About 13% of the MAP sample was single section homes.)  Also, 15 of the 18 NEEM manufacturers are included in this sample, indicating good representation.  Almost 70% of the homes in the sample (34) were built in Oregon facilities, 12 were built in Idaho, and 3 were built in Washington.  Of the Idaho sample, 44% were built in Oregon, 48 % in Idaho and 8% in Washington.  In the Washington sample, all homes but one (23/24) were built in Oregon; the remaining home was built in Washington.

### Manufacturer Information

| Manufacturer | # of homes in sample | % of sample |
| --- | --- | --- |
| Fleetwood-Idaho | 3 | 6.12 |
| Fleetwood-Oregon | 1 | 2.04 |
| Fleetwood-Wash. | 2 | 4.08 |
| Fuqua | 6 | 12.24 |
| Golden West | 4 | 8.16 |
| Guerdon-Idaho | 3 | 6.12 |
| Guerdon-Oregon | 2 | 4.08 |
| KIT | 3 | 6.12 |
| Liberty | 1 | 2.04 |
| Marlette | 5 | 10.20 |
| Nashua | 3 | 6.12 |
| Redman-Oregon | 7 | 14.29 |
| Silvercrest | 4 | 8.16 |
| Skyline | 4 | 8.16 |
| Valley | 1 | 2.04 |
| TOTAL | 49 | 100 |

###### Set-up Compliance

The set-up compliance data table is based on a simple yes/no answer for a checklist of items.  The survey was mostly unchanged from the MAP set-up survey.  Individual states have developed their own set-up standards since MAP, so in some cases the data are not as detailed as would be required by the states.  But in general, structural compliance is near 100%, with the exception of a low score in Idaho for pier support spacing under I-beams (56%).  The “Pier supports installed per manufacturer's markings” field is somewhat obsolete, as most manufacturers do not mark piers as they did in MAP.

Not surprisingly, the lowest overall compliance rate is for belly penetrations, with 54% of all homes in compliance.  This is worse than the MAP rate of 66%.  Idaho’s compliance rate of 29% is especially low.  This is probably a combination of problems occurring at or before time of set-up and subsequent problems (plumbing fixes, etc.).  The MAP and SGC specifications do not offer specific guidance on how to repair these penetrations.  Most crews use some sort of pressure-sensitive tape, and given moisture and dirty surfaces, these tapes tend to fail rather quickly.  The most secure means of ensuring patch success is to use building wrap (such as Tyvek), construction adhesive, and an outstitch stapler.  Weatherization crews often use this technique when blowing insulation into a belly, but set-up crews and servicemen (such as plumbers) are unlikely to go to this much trouble. If the industry converts to blown-in floor insulation, sealing the belly becomes even more critical for energy performance.

Vapor barrier and skirting compliance were effectively 100%.  Windows and doors were found to operate smoothly in most part, but about half of the Washington homes had doors which did not seal against the weatherstripping.  This may account in part for the relative leakiness of Washington homes (see House Tightness section, below).

STRUCTURAL & OPERATIONAL SET-UP COMPLIANCE

| Compliance Issue | % complying in Idaho | % complying in Washington | % complying in both states |
| --- | --- | --- | --- |
| Skirting installed | 100 | 96 | 98 |
| Ground vapor barrier present | 100 | 92 | 96 |
| Pier supports in place under I-beam | 56 | 92 | 73 |
| Pier supports in place under exterior doors | 88 | 100 | 94 |
| Pier supports installed per manufacturer's markings | 90 | 95 | 94 |
| Pier supports capped and shimmed | 87 | 100 | 94 |
| Footings present under pier supports | 100 | 100 | 100 |
| Belly penetrations sealed | 29 | 79 | 54 |
| Marriage line sealed | 70 | 100 | 86 |
| Exterior doors operate smoothly | 92 | 92 | 92 |
| Exterior doors seal against weather-stripping | 83 | 54 | 69 |
| Windows operate smoothly | 88 | 96 | 92 |

Special attention was paid to crossover duct set-up, as problems with the crossover can result in huge energy penalties.  Very low compliance of secure crossover ducts was noted in Idaho.  In most cases, this was because only tape was used to make the connection, the crossover was poorly supported, or there was some combination of these factors.  In a few cases (triple section homes), splitter boxes or tees were poorly connected or even disconnected.  Catastrophic exterior duct leakage (over 500 CFM at 50 Pa) was found in these cases.

The compliance of the crossover duct being connected with sheet metal elbows has risen substantially over the 1995 data  (54.5%), certainly affected by the 1994 MAP specification change requiring sheet metal elbows.  Insulated connections have also risen substantially over the 1995 data (67%).

## CROSSOVER DUCT SET-UP COMPLIANCE

| Compliance issue | % complying in Idaho | % complying in Washington | % complying in both states |
| --- | --- | --- | --- |
| Crossover duct cut to length | 88 | 88 | 88 |
| Crossover duct connections secure | 24 | 92 | 57 |
| Crossover ducts connected w/ sheet metal elbows | 72 | 92 | 82 |
| Crossover duct connections insulated | 92 | 88 | 90 |

House Tightness

A two-point depressurization blower door test (with ducts unsealed) was conducted on all homes.  Duct pressurization tests (with registers sealed and house pressurized to the same level as the ducts with respect to outside) were also conducted and are reported in a later section.

## BLOWER DOOR RESULTS

|  | SGC Mfd Homes 1997-98 (this study) |  |  |  | MAP 1992-93 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Group | # of cases | ACH50 average* | Std. Dev. | CFM50 average | # of cases | ACH50 average | Std. Dev. |
| All | 49 | 4.76 | 0.95 | 1187 | 157 | 5.50 | 1.87 |
| Double Wide | 36 | 4.90 | 0.99 | 1102 | 127 | 5.50 | 1.90 |
| Triple Wide | 13 | 4.40 | 0.72 | 1424 | 12 | 4.92 | 1.22 |
| Idaho | 25 | 4.63 | 0.81 | 1101 | 32 | 6.12 | 1.55 |
| Washington | 24 | 4.90 | 1.08 | 1277 | 62 | 5.36 | 1.77 |

*minimum ACH50 is 2.33; maximum is 8.52

The average ACH50 for homes in this study is much lower than the MAP sample.  Idaho's average ACH50 has improved substantially and is now lower than Washington's ACH50.  Because of high standard deviations and the small sample size, a review of the air changes per hour at 50 Pa separated by home manufacturers is not noted in the report.

The following table is presented in order to place the newest results amidst other house tightness results from recent studies.  Although these manufactured homes still exhibit a moderate amount of shell leakiness, the trend toward a tighter building envelope continues.

## BLOWER DOOR RESULTS FOR NORTHWEST HOMES

| Group (Study Reference) | n | House Type, Year Built | ACH50 (averages) |
| --- | --- | --- | --- |
| WWP, Spokane [Kennedy et al 1994] | 33 | Site-built, "historic" | 14.3 |
| WWP, Spokane [Kennedy et al 1994] | 21 | Mobile home, "historic" | 13.3 |
| NORIS I [Palmiter & Brown 1989] | 134 | Site-built, 1980-86 | 9.28 |
| NORIS II [Palmiter et al 1990] | 49 | Site-built, 1987-88 | 7.18 |
| "Current Practice" Mfd homes [Palmiter et al. 1992] | 29 | Manufactured in late 1980's | 8.75 |
| Super Good Cents Mfd homes [Palmiter et al. 1992] | 131 | Manufactured in late 1980's | 6.10 |
| MAP [Baylon, Davis, Palmiter 1995] | 157 | Manufactured, 1992-93 | 5.50 |
| Super Good Cents Mfd homes (this study) | 49 | Manufactured, 1997-98 | 4.76 |

What are the implications of the level of NEEM tightness for average natural ventilation rates (from stack-induced infiltration/exfiltration)?  If we divide the average ACH50 by 25, the estimated average ventilation rate for this set of homes is 0.19 ACH.  (The tightest home has an estimated ACHnat of 0.09; the leakiest, an estimated ACHnat of 0.34.)  This compares with 0.22 ACH for the MAP homes using the same methodology.  This methodology is an artificial construct, since it says nothing about ventilation rates on a particular day or in specific parts of a home.  Still, it gives a good rough idea of how much infiltration/exfiltration stack will provide on average.  At levels of natural infiltration around 0.20 ACH, an assist is certainly needed from mechanical ventilation to reach levels recommended by ASHRAE.

The average equivalent leakage area (ELA) for this set of homes, as determined by the LBL Stack Method, is still on the order of 60 in2.  That is, there is plenty of shell leakage left to feed exhaust systems (leaving aside the issue of where the leaks are).  The problem is not finding the make-up air for the exhaust systems.  The problem is making sure the systems are properly designed and installed by the manufacturers and are turned on and maintained by the occupants.

Whole House Ventilation System Performance

The ventilation systems reviewed in this study are all based on a central exhaust fan.  HUD’s 1994 ruling on mechanical ventilation barred use of spot ventilators (bathroom fans) for whole house ventilation (HUD 1994).  HUD later explained that fans located in the bathroom were not necessarily disallowed; their intent was to require manufacturers to install a high quality fan than commonly used for the whole house ventilator.  Since the 1994 ruling, some manufacturers have received approval to use a bath fan for whole house ventilation.  As the table shows, the most common location of the whole house fan is the hallway (43% of all cases), with the utility room (22%) the next most common.  A bath fan is used in 20% of the cases.

WHOLE HOUSE FAN DATA

| Location of fan | % in Idaho (n=25) | % in Washington (n=24) | % in both states (n=49) |
| --- | --- | --- | --- |
| Hall | 28 | 58 | 43 |
| Utility room | 28 | 17 | 22.5 |
| Bathroom | 24 | 17 | 20 |
| LR/Fam Rm/DR | 16 | 8 | 12 |
| Kitchen | 4 | 0 | 2 |
| Fans with timers | 24 | 21 | 22.5 |
| Fans with disabled timers | 12 | 0 | 6 |
| Fans w/dedicated breaker on panel | 8 | 0 | 4 |
| Fans controlled by manual switch only | 56 | 79 | 67.5 |

Median measured fan flow is 73 CFM.  No measurable flow was reported in only 4 homes; 2 others had flow of less than 30 CFM, indicating a very dirty fan, obstructed ductwork, or some other problem.  About 75% of the fans had measured flow of 40 CFM or more.

Limited run time is really the issue here.  Even a 40 CFM fan can provide effective ventilation if it is run continuously.  As the chart below shows, 63% of the fans not controlled by an automatic timer (26/41 cases) were turned off at the time of the audit.  In most of these cases, this was the normal operating condition of the fan as ascertained by the auditor.  Only 27% of the homes had whole house fans controlled by an operating timer or dedicated circuit breaker.

A fan moving 70 CFM has to run about 20 hours/day to augment natural ventilation of 0.20 ACH sufficiently to reach the ASHRAE-recommended level of 0.35 ACH.  There are only 3 cases in our set of homes where the fan was run at this level and only 8 homes where the fan was controlled to operate for 8 hours/day or more.  In three of these cases, the Northwest Timer Kit controlled whole house fan operation.

About 20 % of the whole house fans were reported as noisy (next table); several were reported as extremely quiet (while still delivering rated flows).  Several fans were also reported as very dirty (even though they had been installed and operating for a relatively short time).  Fan maintenance is important, but few homeowners think about it or take the time to perform this task.

Lessons are clear:  (#1) Homeowners need to be educated (once again) about the importance of ventilation (especially as homes get tighter), controls need to be labeled (and placed so that the homeowner notices them), and fans need to be operated.  Homes are still leaky enough to provide plenty of air to these fans, but if they are never turned on, the average ventilation rate of many of the homes is quite likely to fall well below ASHRAE-recommended levels.  (#2) Manufacturers must install fans properly and in- plant inspection and quality assurance need to ensure this.

###### WHOLE HOUSE FAN MANUFACTURER

| Maker | n | # reported as noisy |
| --- | --- | --- |
| Broan | 26 | 5 |
| Nutone | 6 | 3 |
| Panasonic | 13 | 0 |
| Unknown/not reported | 4 |  |

Two homes reported strong odor problems, specifically, sewage odors.  In one of these cases, the utility room (containing the gas furnace and gas water heater) had no pass-through grille to the body of the home and the furnace was getting all of its return air from shell leakage (including the plumbing soil stack).  In this home, the utility room was depressurized to 42 Pa with respect to outside.  Even though the water heater was a closed combustion unit, depressurization was so severe that the water heater had difficulty operating.  Carbon monoxide was also re-entrained in the utility room through leaks in the building shell.

Make-up air systems and attic ventilation systems were tallied.  Make-up air systems are intended to provide extra dilution/removal air for indoor pollutants.  Manufactured homes are getting more airtight, but most have sufficient unintentional shell leaks which provide adequate make-up air for whole house ventilation systems.  Leaks, whether intentional or otherwise, need to be combined with an adequate driving force for an adequate amount of time each day to meet air quality standards such as ASHRAE Standard 62.

ATTIC VENTILATION & MAKE-UP AIR SYSTEMS

| Characteristic | # of units |  |  |
| --- | --- | --- | --- |
|  | Idaho | Washington | both states |
| Attic has mechanical venting systems | 11 (44%) | 6 (25%) | 17 (35%) |
| Blend Air (Coleman) | 9 | 5 | 14 |
| VentilAire II (Intertherm) | 2 | 1 | 3 |
| Make up air system type (includes in-operable systems) |  |  |  |
| Blend Air (Coleman) | 4 | 1 | 5 |
| Blend Air w/NW Timer Kit* | 5 | 4 | 9 |
| VentilAire II (Intertherm) | 1 | 5 | 6 |
| Passive Duct (POS or VentilAire I) | 9 | 12 | 21 |
| Make up air system inoperable** | 4 (16%) | 3 (12.5%) | 7 (14%) |
| No make-up air system | 6 (30%) | 2 | 8*** (16%) |
|  | % of homes reviewed which had |  |  |
| Window fresh-air vents | 24 | 13 | 18 |
| Attic passive vents | 100 | 96 | 98 |
| Continuous soffit vents | 54 | 30 | 43 |
| High vents in each section | 67 | 100 | 83 |
| Gable end vents | 36 | 21 | 29 |

*Median run time of whole house exhaust fan for this system was 8 hours.  Two NW Timer Kit systems were disabled so that the whole house fan did not operate.

**Includes two Blend-Airs with Northwest Timer Kits, three Blend-Airs without the Timer Kit, and two with passive inlet ducts with dampers that are screwed shut.

***Out of the 8 cases without make-up air systems, only two, which were in Idaho, did not have window vents. One out of 49 sampled had window vents that were stuck and did not operate.

The Idaho homes had higher measured average indoor relative humidity than Washington (46% vs. 36%).  The average readings are not noteworthy, but it should be noted that a majority of homes in the study were sited east of the Cascades.

Several factors could be contributing to higher relative humidity in some of these homes.  A timer or a dedicated circuit controlled none of the whole-house fans in the eight homes that had above 50% relative humidity.  One of these homes had a wet crawlspace and another has five occupants.  Another home has a dryer that vents to the crawlspace and 8 occupants.  One home has no comments or data that would suggest an obvious reason for the high humidity other than the previously mentioned lack of a whole house fan on a timer.

Heating/Air Conditioning System Data

Distribution of heating system type is much wider in this group of homes than in the MAP impact evaluation.  Only half the homes have a central electric furnace versus about 85% in the MAP sample.  The percentage of heat pumps is about the same in the two samples.  Heating system size is not dictated by the size of the homes or the type of heating system.

Originally, it was thought that only electric heating systems would be included in this study.  But natural gas and LPG furnaces are becoming more common in manufactured homes in the Pacific Northwest because of price advantages and consumer choice.  A significant portion of the sample had other combustion appliances in the home other than a gas or LPG furnace.  Natural gas water heaters were the most common of these appliances (found in 24% of the sample).  Only four homes had a wood stove or wood fireplace; only one had a wood pellet stove.  As a safety measure, combustion appliance flue gases were checked for CO emissions, as was home ambient air.

## HEATING SYSTEM SURVEY

|  | % in Idaho | % in Washington | % in both states |
| --- | --- | --- | --- |
| Has electric furnace | 56 | 42 | 49 |
| Has heat pump (HP) | 4* | 25 | 14 |
| Furnace fired by natural gas or LPG | 40 | 33 | 36 |
| Has central air conditioning (other than HP) | 28 | 46 | 37 |
| % of gas/LPG furnaces with central air conditioning | 40 | 75 | 56 |
| Combustion appliances present** | 40 | 46 | 43 |
|  | kBtu/hr | kBtu/hr | kBtu/hr |
| Average electric furnace size | 50 | 60 | 54 |
| Average heat pump size | 36 | 41 | 40 |
| Average nat. gas or LPG furnace size | 56 | 51 | 54 |

*only one heat pump in Idaho, located in Juliaetta (SE of Moscow)

**other than central natural gas or LPG furnace

Ductwork type was noted, mostly to show the percentage of duct board used in these homes.  Only three homes in this sample used duct board trunk ducts: two Redman homes and one Guerdon-Idaho home.  Another manufacturer, Palm Harbor Homes, uses a duct board system and mastic for sealing joints (unlike Redman or Guerdon) and has achieved good duct tightness results.  Palm Harbor is not represented in this sample.

The table also breaks down duct tape type.  Every plant uses some type of tape to seal joints.  The tape most commonly used before the latter stages of MAP is aluminum tape with a thin (2 mil) acrylic adhesive backing.  A push was made to encourage manufacturers to use aluminum tape with thicker (10 mil) butyl rubber based adhesive.  Each tape can be defeated by a dirty application surface (common) or sharp metal edges (also common); neither tape has much tensile strength and will usually fail if used for a mechanical connection or if applied to a piece of metal which is under spring tension (an incompletely bent finger joint is a common example).  The table shows butyl tape was the primary sealant used in half of the homes; another 11% of homes used a combination of butyl and acrylic tape.

Auditors were asked to evaluate tape for failure.  Failure at supply registers was defined as lack of adhesion at one or more registers; lack of adhesion meant open gaps were visible or a finger could be inserted behind the tape.  Failure at the furnace connection was sometimes hard to observe, but smaller failures here can result in larger energy penalties than at the registers.

Failure rates are substantial for both tapes, and suggest the need to come up with a more reliable means of supporting duct connections and limiting air leakage.  Duct leakage results (below) confirm that a shift to the thicker adhesive tape has had no effect on reducing leakage rates.

## Duct TYPE AND Connections

|  | % of homes reviewed |  |  |
| --- | --- | --- | --- |
| Characteristic | Idaho | Washington | both states |
| Duct Board | 8 | 4 | 6 |
| Sheet Metal | 92 | 96 | 94 |
| Type of tape used at furnace & registers |  |  |  |
| Acrylic | 36 | 46 | 39 |
| Butyl | 55 | 42 | 50 |
| Butyl and Acrylic | 9 | 13 | 11 |
| Tape falling off at furnace | 33 | 17 | 24 |
| Acrylic (% falling off) | 80 | 33 | 24 |
| Butyl (% falling off) | 0 | 33 | 16 |
| Butyl and Acrylic (% falling off) | 20 | 33 | 14 |
| No tape present | 13 | 0 | 6 |
| Tape falling off at registers | 42 | 48 | 45 |
| Acrylic (% falling off) | 33 | 18 | 25 |
| Butyl (% falling off) | 44 | 73 | 60 |
| Butyl and Acrylic(% falling off) | 22 | 9 | 15 |
| No tape present | 5 | 0 | 2 |

Duct leakage data are of particular importance in determining duct losses.  Average duct leakage is considerably higher than the MAP study showed; however, a small number of very leaky cases skew the average.  These are the catastrophic failures where splitter boxes or tees of triple section homes were disconnected, as mentioned on page 4.  For this reason, median values are a better measure of performance.  Medians for SGC homes are quite close to the MAP figures.  This means leakage caused by poor on-site installation has probably increased, and also means leakage rates for ducts installed in the plants have not decreased.  Work remains to be done in the area of duct connections—both in the plants and on-site.

DUCT  LEAKAGE TO EXTERIOR*

|  | ##### SGC Mfd Homes 1997-98 Median (Average) |  | MAP 1992-93 (Averages except for triples) |  |
| --- | --- | --- | --- | --- |
| Group | Leakage @ 25 Pa (ft3/min) | Leakage @ 50 Pa (ft3/min) | ##### Leakage @ 25 Pa (ft3/min) | Leakage @ 50 Pa (ft3/min) |
| All (n=47) | 103 (151) | 159 (231) | (104) | (157) |
| Double section home (n=34) | 97 (157) | 157 (240) | (101);n=124 | (155) |
| Triple section home (n=13) | 144 (134) | 223 (210) | 122; n=11 | 169 |
| Idaho (n=24) | 106 (165) | 168 (254) | - | - |
| Washington (n=25) | 103 (135) | 159 (208) | - | - |

*Leakage back into the home’s interior neutralized by blower door operation

Some additional points are worth noting.  If we compare median leakage rates for homes with ducts sealed with the butyl tape and acrylic tape, the butyl tape group is much leakier:  156 CFM25 (for 21 cases) vs. 93 CFM25 (19 cases).  Ducts attached to electric forced air furnaces (median 113 CFM25 for 24 cases) were leakier than natural gas cases (median 97 CFM25 for 11 cases).  The three leakiest duct systems (437 CFM25, 555 CFM25 and 628 CFM25) were attached to electric furnaces.  The leakiest system was found in a Washington double-section home.  The next six leakiest homes were sited in Idaho; five of these homes were double-section units.

Air handler flow and system static pressure data were collected to enable estimates of duct distribution efficiency.  Idaho used the temperature rise method (nearest register minus return air temperature) and Washington used the Energy Conservatory flow grid (currently under development) to find furnace data.

#### FURNACE AIR FLOW AND SYSTEM STATIC PRESSURE

|  | Mean | Median |
| --- | --- | --- |
| Air handler flow (standard CFM); n=49 | 1,082 SCFM | 1,087 SCFM |
| Static pressure at registers (average of 4 readings); n=39* | 20.3 Pa | 15.6 Pa |
| Static pressure at furnace supply plenum; n=36* | 57.6 Pa | 47 Pa |

*Ten cases were eliminated from the register static mean/median results because the static pressure was measured incorrectly.  In 13 cases, it was not possible to measure the supply plenum static pressure because of access problems.

Static pressure data varied somewhat by furnace size (or, more accurately, by home size).  The smallest furnaces (40,000 Btu/hr bin) correspond to smallest houses, but these homes have fewer registers so the median register and supply plenum static are relatively high: 25 Pa and 59 Pa respectively.  The largest furnaces (60,000 Btu/hr bin) have median supply plenum static of 64 Pa and median register static of 14 Pa.

The supply leakage fraction is the ratio of exterior duct leakage at average system static pressure divided by furnace air handler flow.  The average system static pressure is a weighted average of supply plenum and register static pressures.  For this type of home, the supply plenum static pressure and the average of register statics each receive equal weight.  For example, if the supply plenum static pressure is 50 Pa, and the average register static is 20 Pa, the overall average system static pressure is 0.5*50 Pa + 0.5*20 Pa = 35 Pa.  Several cases for which register statics were measured incorrectly (mostly in Idaho) were taken out of this analysis.

## SUPPLY LEAKAGE FRACTION*

|  | Mean % | ##### Median % |
| --- | --- | --- |
| All (n=33) | 15.4 | 13.8 |
| Double section (n=24) | 14.6 | 12.8 |
| Triple section (n=9) | 17.6 | 14.5 |
| Idaho (n=11) | 12.8 | 8.9 |
| Washington (n=22) | 16.7 | 14.4 |

*Exterior duct leakage as % of air handler flow.

Detailed analysis has not been performed as yet on the system efficiency implications of the supply leakage fraction.  However, first order approximation suggests an average distribution efficiency of around 80% for an SLF of 15% combined with an R-33 cut-in floor.  Overall system efficiency, on average, should then be expected to range from about 80% for an electric furnace system to about 65% for a system heated with an 80% AFUE gas furnace.  Obviously, there is room for improvement, and the most obvious place is the furnace and register boot connections.  Tape alone will not do the job, so SGC must look to permanent mechanical solutions (augmented by better sealants) to bring duct leakage levels down to a level truly befitting SGC designation.  At least one manufacturer already uses an improved register and boot design which promotes a much better connection and facilitates application of mastic (but on a duct board trunk).  This design is not at all experimental, but is now everyday practice at this plant.

Summary of Findings

- Set-up compliance was generally acceptable, but certain problem areas (especially unsealed belly penetrations and crossover connections) remain.

- NEEM manufactured homes are getting tighter; averaging 4.76 ACH50 vs. 5.50 ACH50 for the MAP random sample.

- Small sample size makes drawing a definite conclusion difficult, but it appears duct leakage was not appreciably greater than measured for the MAP homes. Leakage is still substantial, and duct distribution efficiency suffers as a result.  The study results indicate that use of butyl tape has not solved the problem. Better duct connection techniques and materials are needed.

- Homeowners did not customarily operate more than half the whole house ventilation systems.  Only 29% of the systems had an operating timer or dedicated electrical breaker, and only three systems out of 49 were operated continuously.  Central ventilation systems require intentional controls and labeling and homeowners need better information if these systems are to deliver effective ventilation.

References

Baylon, D., B. Davis, L. Palmiter.  1995.  Manufactured Home Acquisition Program:  Analysis of Program Impacts.  Prepared for Bonneville Power Administration under Contract No. DE-AM79-91BP13330, Task Order #71945.

HUD.  1994.  Manufactured Home Construction and Safety Standards.  Revised Part 3280 of Title 24.  United States Department of Housing and Urban Development.

Kennedy, M., P. Francisco, J. Heller, B. Manclark, and L. Palmiter.  1994.  Energy Exchanger Installation Quality Assurance Study.  Prepared for Washington Water Power Company under Contract No. R-0166-93.

Palmiter, L., T. Bond, I. Brown, and D. Baylon.  1992.  Measured Infiltration and Ventilation in Manufactured Homes.  Prepared for Bonneville Power Administration under Contract No. DE-AM79-91BP13330.

Palmiter, L., I. Brown, and T. Bond.  1990.  Northwest Residential Infiltration Study, Cycle II:  Infiltration and Ventilation in New Electrically Heated Homes in the Pacific Northwest.  Ecotope, Inc., Seattle.

Palmiter, L. and I. Brown.  1989.  Northwest Residential Infiltration Study, Volume 1:  Analysis and Results.  Prepared for the Bonneville Power Administration under Washington State Energy Office Subcontract No. 88-24-01.

Acknowledgements

The Northwest Energy Efficiency Alliance, WSU Cooperative Extension Energy Program and the USDOE Building America Industrialized Housing Partnership’s Build America Program supported this project.  Various members of the SGC Technical Committee, especially A.B. Boe, Ken Eklund, David Hales, Tom Hewes, Michael Lubliner, and Paul Tschida, reviewed earlier versions of the report and offered many helpful comments.  Thanks are also due the homeowners who participated in the project.

________________________________________

r:\te\new plan\residential resource assessment\housing stock characteristics & forecast\mhcharacteristics.doc